## Civil Works
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 150mm Thik AAC Block Wall | SQM | 80 | 1750 | 140000
2 | Block Work with Paint | SQM | 140 | 480 | 67200
3 | Builder Walls | SQM | 335 | 480 | 160800
4 | Cement Plastering | SQM | 75 | 500 | 37500
5 | Self levelling (3-5mm thickness) | SQM | 2130 | 350 | 745500
6 | Providing and applying of Plaster of Paris Punning (1st Quality ISI approved POP) over plastered with minimum thickness of 8mm-12mm to existing wall surfaces , column & concrete members etc., to be finished in line and plumb with smooth surface ready to receive paint base. Rate to be inclusive of hacking wall surfaces for better bonding, cleaning, scrubbing the surface, providing grooves if necessary etc., complete as per architect's approval. | SQM | 400 | 310 | 124000
7 | RCC Lintel (for Doors) | RMT | 4.3 | 2143 | 9214.9
8 | Waterproofing (For Floor + Walls 600 mm High) | SQM | 170 | 1050 | 178500
9 | Pest Control and Anti-Termite Treatment | SQM | 2460.4236 | 75 | 184531.7726
10 | Floor chipping upto 100mm thk | SQM | 395 | 300 | 118500
11 | Dismantling of Doors and Partitions | SQM | 40 | 400 | 16000

## Interior Works
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Tile - Type -01 (Size: 600mm X 600mm) | SQM | 365 | 2646 | 965790
2 | Tile Cladding (300mm X 100mm) | SQM | 40 | 2646 | 105840
3 | Providing and finishing of homogenous self leveling epoxy flooring of thickness minimum 3mm with mastertop 1200 of MBT degussa/ardex R70 P in approved colour after surface preperation by shot blasting with vaccine attatchment etc complete the rate should be inclusive of carrying out self levelling, cove upto 100mm high into the wall with solventless epoxy incorporating very high abrasion resistent aggregates and merged with wall levelling on one end floor on other end as per specification of manufacturer/architects. | SQM | 15 | 4802 | 72030
4 | Providing and applying 2–3 mm thick self-leveling, anti-static, chemical-resistant epoxy flooring in AHU, electrical, UPS, hub, battery, and server rooms using a multi-layer epoxy system of approved make. Surface preparation shall include cleaning, grinding, and priming to ensure proper adhesion. Application shall consist of base coat, conductive copper strip/grid (where required), intermediate coat, and a final topcoat in approved shade with semi-gloss/smooth finish. The flooring shall be non-dusting, jointless, easy to maintain, and resistant to moisture, oils, and chemicals. Includes coving at wall junctions up to 100 mm height, finishing around cut-outs, and all necessary edge detailing. Execution to be carried out in accordance with manufacturer specifications and under the supervision of architect. | SQM | 30 | 1176 | 35280
5 | Antistatic Raised Flooring - 300mm Height | SQM | 30 | 4410 | 132300
6 | LVT Wooden Flooring | SQM | 70 | 1960 | 137200
7 | 100mm Gypsum Board Full Height Partition Without Finish - GI Framework (Both Side GYP Board) | SQM | 408 | 2900 | 1183200
8 | Above Door Partition | SQM | 35 | 2900 | 101500
9 | 200mm thick partition for AV Support | SQM | 52 | 4263 | 221676
10 | Gypsum Column Cladding with Ply paneling, as required | SQM | 330 | 1261 | 416130
11 | Decorative Cladding Acoustic Panelling Laminate Panelling Lacquered Glass Panelling | SQM | 350 | 1372 | 480200
12 | Painting for True Ceiling | SQM | 2415 | 265 | 639975
13 | Plain Gypsum board ceiling | SQM | 550 | 1100 | 605000
14 | Acoustic Perforated Wooden ceiling 0.7 NRC | SQM | 15 | 4410 | 66150
15 | Fire Rated modular grid ceiling :- | SQM | 30 | 2058 | 61740
16 | Stretched fabric light false ceiling | SQM | 35 | 16500 | 577500
17 | Acoustic Baffle ceiling | SQM | 13 | 7350 | 95550
18 | Acoustic Cloud ceiling | SQM | 20 | 3430 | 68600
19 | Designer Ceiling - Laminate finish | SQM | 97 | 4410 | 427770
20 | Gyp-roc bondit on true ceiling | SQM | 200 | 539 | 107800
21 | Premium Acrylic Emulsion Paint (Wall / Partitions / Column) | SQM | 2450 | 300 | 735000
22 | Acoustic Panelling | SQM | 95 | 1800 | 171000
23 | Laminate Panelling | SQM | 165 | 2500 | 412500
24 | Lacquered Glass Panelling | SQM | 49 | 4900 | 240100
25 | MDF Paneling with duco paint | SQM | 15 | 3500 | 52500
26 | MDF Fluted Paneling with duco paint | SQM | 13 | 3822 | 49686
27 | Metal TV Design partition | SQM | 45 | 3430 | 154350
28 | 50mm HT Aluminium Wall Skirting | RMT | 850 | 294 | 249900
29 | Fluted Paneling/Cladding | SQM | 330 | 2891 | 954030
30 | Corner Guard | RMT | 700 | 245 | 171500
31 | Reception Wall Backdrop | SQM | 20 | 8330 | 166600
32 | Reception Table 2100mm X 900mm X 1000mm | NOS | 1 | 250000 | 250000
33 | Fabric Paneling with Wooden Frame | SQM | 18 | 8330 | 149940
34 | TV Unit | SQM | 20 | 7350 | 147000
35 | Boardroom Table (5400mm X 1800mm) | NOS | 1 | 250000 | 250000
36 | Boardroom Serving Counter (5400mm X 850mm X 850mm) | NOS | 1 | 73500 | 73500
37 | Counter Size 01-850mm H 750mm D 4080mm L Water dispenser unit Size 01-2400mm H 750mm D 600mm L | NOS | 1 | 73500 | 73500
38 | 850mm H 750mm D 3850mm L Water dispenser unit Size 02-2400mm H 750mm D 600mm L | NOS | 1 | 73500 | 73500
39 | 850mm H 700mm D 3070mm L | NOS | 1 | 44100 | 44100
40 | Overhead Storage and Wall shelf with cove light | NOS | 1 | 53900 | 53900
41 | Tuk Shop Serving counter - Size -1050mm X 750mm X 2890mm | NOS | 1 | 205800 | 205800
42 | Tuk Shop Wet counter - Size -850mm X 750mm X 2330mm | NOS | 1 | 176400 | 176400
43 | Ledge Seating | RMT | 15 | 11760 | 176400
44 | High Table | NOS | 1 | 52920 | 52920
45 | Window Sill finished with Laminate - 150mm (D) x 600mm (H) (+/-50mm) | RMT | 230 | 1519 | 349370
46 | Pelmet 150mm X 1400mm | RMT | 230 | 1250 | 287500
47 | Booth Seating | NOS | 2 | 127400 | 254800
48 | Ledge Seating | NOS | 2 | 43610 | 87220
49 | Display (Shelves) | SQM | 4 | 15190 | 60760
50 | Providing, fabricating, and installing low height storage unit made of 18 mm thick pre-laminated particle board finished with laminate in approved shade, with 2 mm PVC edge banding on all exposed edges. Overall height to be maintained at 1050 mm from finished floor level, with rounded edges as per approved design. The unit shall include internal shelves/shutters/drawers as per approved drawings, necessary hardware such as hinges, handles, locks, channels, and supports, complete with cutting, fixing, alignment, finishing, and installation at site. | NOS | 2 | 34300 | 68600
51 | 18 mm thick prelaminated particle board finished with laminate in approved shade with 2 mm PVC edge banding on all exposed edges. Table height to be maintained at 1050 mm from finished floor level with rounded edges. | NOS | 1 | 14700 | 14700
52 | Size -600 X 600mm | NOS | 4 | 5537 | 22148
53 | Size -450X 450mm | NOS | 15 | 4551 | 68265
54 | Slotted angle racks - 950mm X 450mm X 2100mm | NOS | 5 | 7700 | 38500
55 | Ply supports for decorative light fixtures / Ply HVAC grills / Service | SQM | 15 | 1421 | 21315
56 | DB shuttering finished with laminate - 300mm to 450mm deep | SQM | 25 | 10780 | 269500
57 | Entrance Mat | SQM | 5 | 4778 | 23890
58 | 3 in 1 Dustbin | NOS | 3 | 30380 | 91140
59 | SS finish Dustbin | NOS | 10 | 2940 | 29400
60 | Compactor (Rack Size - 1500mm X 450mm X 2200mm ) | NOS | 6 | 50000 | 300000
61 | Core cutting - 150mm to 250mm dia | NOS | 10 | 2940 | 29400
62 | Expansion Joints | RMT | 10 | 30000 | 300000
63 | Platform for Collab Area – 150 mm Height | SQM | 68 | 3500 | 238000
64 | Sun control flim | SQM | 30 | 1029 | 30870
65 | Aluminium transition Strips - 25mm to 30mm wide | RMT | 400 | 285 | 114000
66 | Aluminium trims - 6mm X 6mm | RMT | 130 | 177 | 23010
67 | Closing / covering of junction boxes as per site condition | SQM | 10 | 5390 | 53900
68 | Chequered plate for closing of shafts | SQM | 5 | 4410 | 22050
69 | Metal Key Storage - 900mm x 900mm | NOS | 2 | 17150 | 34300
70 | Security Staff | LS | 1 | 78400 | 78400
71 | Professional Deep Cleaning | SQM | 2460.4236 | 105 | 258344.4816
72 | Regular Housekeeping During Project Execution | LS | 1 | 400000 | 400000
73 | Site Office | LS | 1 | 38710 | 38710
74 | Site Storage | LS | 1 | 78400 | 78400
75 | Floor Protection | SQM | 2460.4236 | 63 | 155006.689
76 | Debris Removal | LOADS | 20 | 7350 | 147000

## Modular Glass Partition & Doors
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Single Glazed Partition | SQM | 120 | 4500 | 540000
2 | Above Glass partition | SQM | 75 | 4150 | 311250
3 | 1000mm X 2400mm - Single leaf door (FRD) with vision panel | NOS | 6 | 40000 | 240000
4 | Door Size : 1000mm X 2400mm - with Vision Panel | NOS | 2 | 29500 | 59000
5 | Door Type - D1 1500mm x 2400mm Double Leaf Single Glazed Door. | NOS | 2 | 78000 | 156000
6 | Door Type - D2 1000mm x 2400mm Single Leaf Single Glazed Door. | NOS | 20 | 45000 | 900000
7 | Door Type - D3 750mm x 2400mm Single Leaf Single Glazed Door Sliding Door | NOS | 2 | 43000 | 86000
8 | Door Type - D4 1800mm x 2400mm Single Leaf Single Glazed Double Door | NOS | 2 | 83000 | 166000

## Graphics and Films
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Graphics / Branding – Wall & Partition | SQM | 290 | 1700 | 493000
2 | Size: 600mm X 450mm | NOS | 10 | 1750 | 17500
3 | Size: 1500mm X 900mm | NOS | 5 | 2850 | 14250
4 | Primer for Wallpaper / Graphics | SQM | 290 | 120 | 34800
5 | Frost Film | SQM | 100 | 1450 | 145000

## Blinds
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply & Installation of manually operated roller blinds as per approved style and shade | SQM | 720 | 1050 | 756000
2 | Supply & Installation of motorised roller blinds as per approved style and shade | SQM | 30 | 5000 | 150000

## Planters
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | FRP planter 1 Size: 300-450 dia x 900mm High. species : Schefflera arboricola Xanadu - Medium Dwarf Umbrella Tree. | NOS | 10 | 2800 | 28000
2 | FRP planter 2 Planter Size: 450 dia x 900-1050mm High. Plant Species : Schefflera arboricola Dwarf Umbrella Tree. | NOS | 5 | 4000 | 20000
3 | Planter Material : Wonido Plant Pot Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Size : Height 85 mm Diameter 38 mm Plant White Tulips (Cut Flowers) | NOS | 12 | 5000 | 60000
4 | Planter Material : Wonido Plant Pot Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Size : Height 55 cm Diameter 50 cm Matt White with Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Plant: Lady Palm — Rhapis excelsa. Areca Palm (Dypsis lutescens) Ficus benjamina | NOS | 10 | 5000 | 50000
5 | Planter Material : Wonido Plant Pot Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Size : Height 75 cm Diameter 42 cm Matt White with Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Plant: Dieffenbachia Green Magic Dieffenbachia Green Magic Philodendron Sellom (Medium) Heart Leaf Money Plant | NOS | 10 | 4000 | 40000
6 | Planter Material : Wonido Plant Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Size : Height 100MM Diameter 150MM HIGH Matt White with Removable Plant Insert for Indoor and Outdoor Use Made of High-Quality Polypropylene. Plant: Dieffenbachia Green Magic Teardrop Peperomia Varigated Turtle Vine (Callisia Repens) MONEY PLANT Marble Queen Philodendron Sellom | NOS | 8 | 5500 | 44000

## Carpet Flooring
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Carpet Type - 1 | SQM | 1291.5 | 2150 | 2776725
2 | Carpet Type - 2 | SQM | 53 | 2750 | 145750
3 | Carpet Type - 3 | SQM | 231 | 2150 | 496650

## Modular Furniture
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Workstation Linear Sharing/Non sharing - 1500mm X 750mm | NOS | 305 | 13500 | 4117500
2 | 4 Pax MR Table (1500mm x 900mm x 750mm ) | NOS | 5 | 21000 | 105000
3 | 6 Pax MR Table ( 2100mm x 1050mm X 750mm) | NOS | 1 | 29450 | 29450
4 | 8 Pax MR Table ( 3000mm x 1100mm x 750mm) | NOS | 2 | 39000 | 78000
5 | 4 Pax MR Table (900mm (dia) x 750mm ) | NOS | 1 | 12795 | 12795
6 | 12 Pax Conference Room Table ( 4500mm X 1200mm) | NOS | 1 | 75000 | 75000
7 | Cabin Table | NOS | 6 | 25500 | 153000
8 | AV Rack Storage ( 1000mm X 600mm X 1200mm) | NOS | 1 | 17500 | 17500
9 | Repro Table 650mm Deep, 850mm High: Custome Made Table. | NOS | 2 | 15850 | 31700
10 | TOP: 19MM Thick Prelaminated Particle Board with 2MM PVC edge band on all edges CARCASS (Body/ Shutter / Back) : 19 MM thick Prelaminated Particle Board with PVC edge band on all exposed edges. SHELF : One adjustable and One fixed shelf made of 18MM thick Prelaminated Particle Board with PVC edge band on all edges SHUTTERS : Lockable Swing shutters with Finger Groove HARDWARE : Hettich Hinges, Lock | NOS | 20 | 20000 | 400000
11 | Type 01- 1500mm x 750mm x 750mm | NOS | 5 | 12855 | 64275
12 | Type 02-2100mm x 900mm x 750mm | NOS | 3 | 21000 | 63000
13 | Type 03-950mm x 950mm x 750mm | NOS | 2 | 10500 | 21000
14 | Low Height Storage - 2200mm X 750mm X 850mm | NOS | 2 | 33000 | 66000
15 | Reception planter box (1850mm X 1400mm x 450mm) | NOS | 1 | 38500 | 38500
16 | Booth Table (700mm X 700mm X 750mm) | NOS | 2 | 6500 | 13000
17 | High table for Call booth (1400mm X 500mm X 1050mm ) | NOS | 2 | 10000 | 20000
18 | Book Shelf collab area (3400mm X 500mm X 2400mm ) | NOS | 1 | 105600 | 105600

## Loose Furniture & Chairs
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Center Table-01 - 1300mm x 750mm | Nos | 5 | 13250 | 66250
2 | Coffee Table Collab and Wellness Room - Dia. 600mm | Nos | 5 | 8000 | 40000
3 | Center Table-02 Collab Area - Dia. 900mm | Nos | 2 | 12145 | 24290
4 | 3 Seater Sofa-01 - 1800 mm x 900 mm x 800 mm | Nos | 1 | 50000 | 50000
5 | 3 Seater Sofa-02 - 2400 mm x 900 mm x 800 mm | Nos | 2 | 61500 | 123000
6 | 2 Seater Sofa - 1400 mm x 750 mm x 800 mm | Nos | 1 | 38000 | 38000
7 | Lounge Sofa/Chair-01 | Nos | 2 | 13000 | 26000
8 | Lounge Sofa/Chair-02 | Nos | 2 | 15500 | 31000
9 | Lounge Sofa/Chair-03 | Nos | 6 | 10700 | 64200
10 | Wellness Lounge Chair | Nos | 2 | 13000 | 26000
11 | Chair Cafeteria and Collab Area-01 | Nos | 30 | 2800 | 84000
12 | High Chair Cafeteria Type-01 | Nos | 5 | 3300 | 16500
13 | High Chair Collab Area Type-02 | Nos | 8 | 3300 | 26400
14 | High Chair Call Booth Type-03 | Nos | 4 | 8500 | 34000
15 | High Chair Collab Area Type-04 | Nos | 2 | 8500 | 17000
16 | Chair Cafeteria Chair Type-2 | Nos | 8 | 5800 | 46400
17 | Reception | Nos | 2 | 8800 | 17600
18 | Workstations | Nos | 305 | 8800 | 2684000
19 | Meeting Room 4,6,8 Pax | Nos | 45 | 8800 | 396000
20 | Conference/Board Room | Nos | 20 | 16500 | 330000
21 | Cabin Main chair | Nos | 6 | 11000 | 66000
22 | Cabin visitor chair | Nos | 12 | 8800 | 105600
23 | Meeting room 12pax | Nos | 12 | 13200 | 158400
24 | Bed - Wellness Room | Nos | 2 | 18000 | 36000
25 | Chess board with table | Nos | 2 | 9000 | 18000
26 | Two-Seater Laminated Phone Booth | Nos | 2 | 500000 | 1000000
27 | Single Seater Laminated Phone Booth | Nos | 2 | 280000 | 560000
28 | Bean Bag (L/XL Size) | Nos | 2 | 4000 | 8000

## PHE
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply, Installing, testing and commissioning of Stainless sink with single bowl manufactured from 1mm thick stainless steel, 18G high grade indestructible chrome nickel steel with top quality polish,1no.40mmdia CP waste coupling, Sink cock with wall flange with aerator etc., complete. For Kitchen/Cafe/Wet Pantry. | NOS | 2 | 6600 | 13200
2 | Supply, Installing, testing and commissioning of 15 mm dia CP Angle cocks (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning)complete. | NOS | 2 | 840 | 1680
3 | Lifting Station - pre-fabricated package unit, 1.5 kW, vertical lift up to 7 m Make: Sulzer / Wilo / Grundfos / Saner Greywater Pre-fabricated polyethylene tank with built-in pump + check valve + control panel Capacity: ~50 L holding + 1.5 kW pump @ 2.5 m³/hr Float-switch auto operation, dry-run protection, alarm + visual indicator Inlet 110 mm UPVC SWR, Outlet 50 / 75 mm pressurised line to stack 230V single-phase, with control panel + cabling INCLUDES: tank + pump + check valve + control panel + alarm + connections | NOS | 2 | 150000 | 300000
4 | Lifting Station Outlet Pressurised Line - CPVC / GI to nearest stack inlet 50 mm CPVC / GI pressurised pipe, ~10 m run with check valve + isolation | NOS | 1 | 30000 | 30000
5 | Lifting Station Power + Alarm Wiring - to LV / Plumbing DB 230V single-phase supply + alarm relay to BMS / monitoring | NOS | 1 | 12500 | 12500
6 | 40mm dia (low noise pipe) | RMT | 20 | 216 | 4320
7 | Supply and fixing of PVC self cleasing, deep seal type 110 mm dia Multi Floor trap and 75mm outlet with necessary cement concrete, water proofing the internal surfaces of chamber etc.,or laid under floor / under ceiling / on walls with suitable clamps including making bores in masonry etc., and rendering the bores in cement mortar after laying the pipes and specials curing etc., complete as per specifications. depth of trap shall not be less than 125mm.(The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning) complete | NOS | 1 | 540 | 540
8 | Supply, fixing and testing of Garbodrain G-1000 (Food waste crusher), including all fittings, should be anti-jam impellers made of SS 304 for efficient grinding & corrosion free, run with AC power supply with calling bell switch for dry run protection. (for cafeteria plate wash counter sink area) | NOS | 1 | 19200 | 19200
9 | SFA-Grease separator below counter (grease trap Undersink, Standard, or equivalent,.), café plate wash sink area. | NOS | 1 | 32400 | 32400
10 | 20mm Dia | RMT | 20 | 162 | 3240
11 | 20mm Dia | NOS | 1 | 1080 | 1080

## Light Fixtures
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Decorative Hanging Light Type 01 | NOS | 55 | 4500 | 247500
2 | Decorative Hanging Light Type 02 | NOS | 12 | 6500 | 78000
3 | Decorative Wall Light Type 03 | NOS | 3 | 3500 | 10500
4 | Decorative Neon Wall Light Type 04 - 1200 mm x 750 mm | NOS | 1 | 130000 | 130000
5 | Suspended Hanging Light | RMT | 30 | 3200 | 96000
6 | "Providing and fixing flexible LED strip lights with aluminum profile, polycarbonate diffuser, LED driver, and all electrical connections complete as per approved detail and layout.The strips shall be high-efficiency, low-power consumption type with uniform illumination and long life (minimum 50,000 burning hours). For indoor areas the LED strips shall emit neutral to warm white light (3000–4000 Kelvin) to create a comfortable and welcoming ambience. Indoor strip light, 5Watts/Mtr, 5Mtr Reel , 24V DC, 3SDCM - PRIME WITH Surface Mount Aluminum Profile W: 16mm X H: 18mm Standard length -3 meter and 5 Nos Electronic Driver | RMT | 28 | 550 | 15400
7 | Supply of recessed mounted 2X2 LED panel ,made of CRCA housing with high efficiency PS Diffuser. LED Used shall be SMD type and fixture should have minimum efficacy at System level >=100 lumens/watt with Minimum system Lumens 3600 & Max , Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance,CCT-4000K/5700K/6500K, (SDCM<=5), CRI Ra >=80, THD<10%, PF >0.95, an operating Voltage Range of 140 - 270 VAC.Minimum Internal Surge Protection 3.0KV & IP20/IK02 protection, Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval . | NOS | 7 | 2275 | 15925
8 | Extruded aluminium suspended linear LED, white/black powder-coated finish, high-efficiency opal diffuser, width not more than 50 mm ±3 mm, SMD LED, approx. 2200 lm ±10%, efficacy 100 lm/W, 4000K, CRI 80, PF ≥0.95, THD ≤10%, 140–270V AC, Class I protection, Class B serviceability, 3.5kV surge protection, LM79/LM80 documentation, suspension kit, supply and installation complete | NOS | 185 | 4200 | 777000
9 | Recessed LED Downlighter ,made up of pressure die cast aluminum housing with high efficiency PS diffuser, LED Used shall be SMD type and fixture should have minimum efficacy at System level 120 lumens/watt with Minimum system Lumens 1200 , CCT of 4000K (SDCM<=5), CRI Ra >=80, PF >0.9, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 160-270 V AC. Minimum Internal Surge Protection 2.5KV. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. | NOS | 285 | 595 | 169575
10 | Supply of Suspended Cylinderical Downlight, 1000 lm, Having CCT option of 4000K, SDCM<5, CRI≥80, Efficacy ≥100lm/W, Surge 2.5kV internal, THD ≤10% (At Full Load), pf ≥0.9. The luminaire housing shall be Extruded aluminum housing, White/Black finish , Product Dia 55mm, Height 150mm. The product should have beam angle option of 40° beam angle. The operating volateg range shall be 140-270V. The product shall be Class B serviceability. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. | NOS | 250 | 1750 | 437500
11 | Cove lighting of size 100mm to 150mm x 100mm to 150mm | RMT | 30 | 1000 | 30000

## Electrical
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | MAIN PANEL 1 | NOS | 1 | 710708 | 710708
2 | 85 KVA APFC Panel as per shown in the SLD Drawing. | NOS | 1 | 305000 | 305000
3 | UPS INPUT/OUTPUT Panel as per shown in the SLD Drawing for 80 KVA UPS | NOS | 1 | 305000 | 305000
4 | 3.5 Core X 300 Sqmm | MTS | 50 | 1500 | 75000
5 | End terminations | NOS | 2 | 2200 | 4400
6 | 3.5 Core X 150 Sqmm | MTS | 120 | 1210 | 145200
7 | End terminations | NOS | 4 | 1925 | 7700
8 | 3.5 Core X 95 Sqmm | MTS | 20 | 990 | 19800
9 | End terminations | NOS | 2 | 1210 | 2420
10 | 4 Core X 70 Sqmm | MTS | 30 | 850 | 25500
11 | End terminations | NOS | 2 | 990 | 1980
12 | 4 Core X 16 Sqmm | MTS | 150 | 300 | 45000
13 | End terminations | NOS | 6 | 715 | 4290
14 | 4 Core X 10 Sqmm | MTS | 535 | 245 | 131075
15 | End terminations | NOS | 24 | 550 | 13200
16 | 4 Core X 6 Sqmm | MTS | 150 | 250 | 37500
17 | End terminations | NOS | 6 | 550 | 3300
18 | 4 Core X 4 Sqmm | MTS | 175 | 220 | 38500
19 | End terminations | NOS | 12 | 550 | 6600
20 | 1 Core x 70 Sq. mm | MTS | 200 | 1825 | 365000
21 | End terminations | NOS | 18 | 830 | 14940
22 | 1 Core x 16 Sq. mm | MTS | 200 | 852 | 170400
23 | End terminations | NOS | 18 | 330 | 5940
24 | 1 Core x 10 Sq. mm | MTS | 150 | 368 | 55200
25 | End terminations | NOS | 12 | 330 | 3960
26 | 1 Core x 6 Sq. mm | MTS | 30 | 320 | 9600
27 | End terminations | NOS | 2 | 250 | 500
28 | 1 Core x 4 Sq. mm | MTS | 60 | 240 | 14400
29 | End terminations | NOS | 2 | 190 | 380
30 | 1 Core x 2.5 Sq. mm | MTS | 250 | 200 | 50000
31 | End terminations | NOS | 16 | 160 | 2560
32 | 1 Core x 1.5 Sq. mm | MTS | 150 | 120 | 18000
33 | End terminations | NOS | 8 | 120 | 960
34 | 3 Core x 6 Sq. mm | MTS | 355 | 225 | 79875
35 | End terminations | NOS | 12 | 440 | 5280
36 | 3 Core x 4 Sq. mm | MTS | 130 | 215 | 27950
37 | End terminations | NOS | 8 | 330 | 2640
38 | 3 Core x 2.5 Sq. mm | MTS | 180 | 150 | 27000
39 | End terminations | NOS | 8 | 330 | 2640
40 | 4 Core x 10 Sq. mm | MTS | 40 | 650 | 26000
41 | End terminations | NOS | 4 | 330 | 1320
42 | 4 Core x 6 Sq. mm | MTS | 50 | 450 | 22500
43 | End terminations | NOS | 2 | 330 | 660
44 | 4 Core x 4 Sq. mm | MTS | 50 | 350 | 17500
45 | End terminations | NOS | 2 | 330 | 660
46 | 2C x 1.5 smm | MTS | 50 | 150 | 7500
47 | SITC pulling of RG-6 coaxial cable, centre copper conductor with foam Shielded jelly filed (Make - Comscope ) pulling through 20mm M.S pipes including all conduit accessories like JBs pull boxes bends fish wire etc as directed by the engineer incharge . | MTS | 120 | 120 | 14400
48 | SITC of RG-11 coaxial cable , centre copper conductor with foam Shielded jelly filed (Make - Comscope ) pulling through 20mm M.S pipes as directed by the engineer incharge . | MTS | 60 | 250 | 15000
49 | SITC of 2 way splitter proper fixture inside and earthing screw provision.splitters in die cast Alum. casing.( Make - Diamond/Triax) with required Baloon Pins ( Shall be provided with Switch (Amplifier )(Note:Splitter should be 2100 to 2400 mHZ) | NOS | 6 | 1000 | 6000
50 | SITC of 1 way splitter proper fixture inside and earthing screw provision.splitters in die cast Alum. casing.( Make - Diamond/Triax) with required Baloon Pins ( Shall be provided with Switch (Amplifier ) | NOS | 6 | 750 | 4500
51 | RG11 F2F connector | NOS | 9 | 150 | 1350
52 | RG06 F2F connector | NOS | 9 | 90 | 810
53 | Lighting /RawPower DBS | NOS | 3 | 33000 | 99000
54 | FLOOR RAW POWER DB CAFE DB | NOS | 1 | 25500 | 25500
55 | FLOOR COMPUTER POWER DB | NOS | 3 | 33000 | 99000
56 | EMERG. LIGHTING DB | NOS | 2 | 12500 | 25000
57 | FLOOR LIGHTING DB | NOS | 3 | 28500 | 85500
58 | FLOOR HVAC POWER DB | NOS | 1 | 25500 | 25500
59 | FLOOR HVAC POWER DB | NOS | 1 | 22350 | 22350
60 | HUB ROOM DB | NOS | 1 | 8500 | 8500
61 | SERVER DB | NOS | 1 | 22050 | 22050
62 | FLOOR LV DB for FAS/PA/BMS/Fire Damper wiring | NOS | 1 | 12500 | 12500
63 | FLOOR AV DB | NOS | 1 | 12500 | 12500
64 | FLOOR 20 KVA UPS O/P DB | NOS | 1 | 25000 | 25000
65 | 200mm W X 100mm D | NOS | 20 | 1427 | 28540
66 | 150mm W X 100mm D | NOS | 20 | 1255 | 25100
67 | 100mm W X 100mm D | NOS | 20 | 1085 | 21700
68 | 40/32A DP MCB/10kA with Weather Proof GI enclosure with all required supporting accessories. | NOS | 2 | 4500 | 9000
69 | 20/25A DP RCCB 100 mIliAmps with Weather Proof GI enclosure with all required supporting accessories. | NOS | 6 | 3800 | 22800
70 | 160A 4P MCCB TM /16kA with GI enclosure with indicating lampe with all required supporting accessories. | NOS | 2 | 28500 | 57000
71 | 63A 4P MCCB/16KA with GI enclosure with indicating lampe with all required supporting accessories. | NOS | 2 | 14000 | 28000
72 | 16A DP MCB/10kA with Weather Proof GI enclosure with all required supporting accessories. | NOS | 2 | 2800 | 5600
73 | Supply & Installation of 3Cx2.5Sq.mm multicore unarmoured flexible cable as lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / sensor / light point and looping between the switches & sensor ( further onwards, it shall be deemed to be included in point wiring). | MTS | 4000 | 140 | 560000
74 | Supply & Installation of 3Cx1.5Sq.mm multicore unarmoured flexible cable as emergency lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / sensor / light point and looping between the switches & sensor ( further onwards, it shall be deemed to be included in point wiring). | MTS | 1000 | 110 | 110000
75 | Supply & Installation of 3Rx1.5Sq.mm multistrand copper conductor wires in 20mm dia MS conduit | MTS | 600 | 110 | 66000
76 | Supply & Installation of 3C x 4 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white colour for UPS circuit and black colour for raw power circuit. | MTS | 250 | 200 | 50000
77 | Supply & Installation of 3C x 2.5 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white colour for UPS circuit and black colour for raw power circuit. | MTS | 4500 | 175 | 787500
78 | Supply & Installation of 3C x 4 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white colour for UPS circuit and black colour for raw power circuit. | MTS | 100 | 220 | 22000
79 | Supply & Installation of 3C x 4 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in existing raceway / conduit | MTS | 70 | 220 | 15400
80 | 1x6A socket controlled by 6A switch | NOS | 20 | 615 | 12300
81 | 3x6/16A socket controlled by 16A switch + 1x6/16A socket controlled by 16A switch - UPS | NOS | 335 | 1100 | 368500
82 | 2x6/16A socket controlled by 16A switch + 1x6/16A socket controlled by 16A switch - Raw | NOS | 330 | 1000 | 330000
83 | 2x6A socket controlled by 16A switch | NOS | 17 | 850 | 14450
84 | 1x6/16A socket controlled by 16A switch | NOS | 42 | 650 | 27300
85 | 1x16A socket controlled by 16A switch (3 Module/4Module) | NOS | 175 | 650 | 113750
86 | 8module MS/GI back box for electrical outlets as per site requirement including necessary civil works | NOS | 5 | 165 | 825
87 | 6module MS/GI back box for electrical outlets as per site requirement including necessary civil works | NOS | 12 | 132 | 1584
88 | 3module MS/GI back box for electrical outlets as per site requirement including necessary civil works | NOS | 20 | 110 | 2200
89 | SITC of MS/GI back box for data outlets as per site requirement including necessary civil works | NOS | 80 | 110 | 8800
90 | 1No. 16A 3 pin 1phase Industrial type socket controlled by 16A MCB with plug top enclosed in sheet metal box with able to mount on wall / raceway with necessary accessories complete as required | NOS | 4 | 1320 | 5280
91 | 20A 3pin 1phase Industrial interlocking socket with plug top controlled by 20A DP MCB - Raw power | NOS | 3 | 4400 | 13200
92 | 32A 5pin 3phase Industrial interlocking socket with plug top controlled by 32A 4P MCB - Raw power | NOS | 4 | 7150 | 28600
93 | FLOOR BOX-2 FOR 16Pax Room -2nos of 6/16A Round pin socket controlled by 1 no. 16 A switch +HDMI | NOS | 4 | 7500 | 30000
94 | POP-UP BOX FOR 12 PAX MEETING ROOM -3nos of 6A Round pin socket controlled by 1 no. 16 A switch+ USB C type +LAN Port RJ45+ HDMI Slot. | NOS | 10 | 13000 | 130000
95 | POP-UP BOX FOR MEETING ROOM -3nos of 6A Round pin socket controlled by 1 no. 16 A switch+ USB C type +2 nos LAN Port RJ45+ HDMI Slot. | NOS | 12 | 13000 | 156000
96 | POP-UP BOX FOR Cabins - 4nos of 6A Round pin socket controlled by 2 no. 16 A switch+ USB C type +2 nos LAN Port RJ45+ HDMI Slot. | NOS | 12 | 14000 | 168000
97 | POP-UP BOX FOR Loose Furniture -1 # 6Amps Socket with 1 Nos. switch for Portable Screan | NOS | 7 | 2500 | 17500
98 | I. Primary light point means wiring from first switch control to the first light out let. | NOS | 150 | 1320 | 198000
99 | I. Secondary light point means extention of light out let only from existing. Primary point to be controlled by the existing switch of Primary point only. | NOS | 450 | 935 | 420750
100 | POINT WIRING - POWER/MCB Control | NOS | 15 | 1850 | 27750
101 | PRIMARY POWER POINT USING 3Cx2.5 Cu XLPE FlEXIBLE CABLE | NOS | 199 | 1320 | 262680
102 | I. Secondary power point means extension of power outlet from existing primary point with ceiling rose & complete accessories. Same to be controlled by the existing MCB in DB | NOS | 848 | 1045 | 886160
103 | 200 x 50mm Size tray | MTS | 65 | 1045 | 67925
104 | 450 x 60mm Size tray | MTS | 15 | 2450 | 36750
105 | 300 x 60mm Size tray | MTS | 10 | 1650 | 16500
106 | 200 x 60mm Size tray | MTS | 80 | 2090 | 167200
107 | 150 x 60mm Size tray | MTS | 23 | 1650 | 37950
108 | 100 x 60mm Size tray | MTS | 25 | 1320 | 33000
109 | 200 x 60mm Size tray | MTS | 30 | 1350 | 40500
110 | 150 x 60mm Size tray | MTS | 20 | 1150 | 23000
111 | 450 x 60mm Size tray | MTS | 15 | 1750 | 26250
112 | 600 x 200mm Size | MTS | 15 | 3190 | 47850
113 | 100 x 40mm | MTS | 720 | 750 | 540000
114 | 50 x 40mm | MTS | 210 | 550 | 115500
115 | 450 x 60mm Size | MTS | 14 | 2200 | 30800
116 | 300 x 60mm Size | MTS | 65 | 1980 | 128700
117 | 200 x 60mm Size | MTS | 90 | 1540 | 138600
118 | 150 x 60mm Size | MTS | 60 | 1375 | 82500
119 | 100 x 60mm Size | MTS | 40 | 1100 | 44000
120 | 450 x 100mm Size | MTS | 8 | 2640 | 21120
121 | 300 x 100mm Size | MTS | 50 | 2200 | 110000
122 | 150 x 100mm Size | MTS | 14 | 1595 | 22330
123 | 500 x 500 x 100mm Size | NOS | 3 | 4400 | 13200
124 | 350 x 350 x 100mm Size | NOS | 6 | 3520 | 21120
125 | 300 x 300 x 100mm Size | NOS | 3 | 3300 | 9900
126 | 250 x 250 x 100mm Size | NOS | 6 | 3025 | 18150
127 | 200 x 200 x 100mm Size | NOS | 3 | 2750 | 8250
128 | 150 x 150 x 100mm Size | NOS | 6 | 2420 | 14520
129 | 500 x 500 x 50mm Size | NOS | 4 | 1980 | 7920
130 | 350 x 350 x 50mm Size | NOS | 45 | 1320 | 59400
131 | 300 x 300 x 50mm Size | NOS | 4 | 1155 | 4620
132 | 250 x 250 x 50mm Size | NOS | 10 | 990 | 9900
133 | 200 x 200 x 50mm Size | NOS | 25 | 825 | 20625
134 | 150 x 150 x 50mm Size | NOS | 115 | 715 | 82225
135 | 110 x 110 x 50mm Size | NOS | 20 | 605 | 12100
136 | 32mm dia | MTS | 30 | 99 | 2970
137 | 25mm dia | MTS | 1550 | 88 | 136400
138 | 20mm dia | MTS | 20 | 75 | 1500
139 | 19mm dia. Single Rod type Maintenance Free Earth pits. Rate shall include 450mm x 450mm x 300mm brick masonry chamber with CI frame and CI cover etc., complete. Eathing system shall be installed as per supplier guidelines /details. MS plate to be provided for each earth pit for its nomenclature. | NOS | 2 | 20200 | 40400
140 | 8 SWG GI Wire | MTS | 240 | 110 | 26400
141 | 50 x 6mm GI Earth flat | MTS | 150 | 220 | 33000
142 | 25 x 3mm GI Earth flat | MTS | 250 | 220 | 55000
143 | Busbar of 0.5 Mtr length made out of 25 x 3 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators along with glass enclosure. | NOS | 4 | 990 | 3960
144 | Busbar of 0.5 Mtr length made out of 50 x 3 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators along with enclosure. | NOS | 1 | 1320 | 1320
145 | Busbar of 0.5 Mtr length made out of 50 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators along with glass enclosure. | NOS | 1 | 1850 | 1850
146 | 1 Core x 70Sq. Mm | MTS | 60 | 506 | 30360
147 | End terminations | NOS | 4 | 605 | 2420
148 | 1 Core x 16Sq. Mm | MTS | 50 | 385 | 19250
149 | End terminations | NOS | 4 | 550 | 2200
150 | 1 Core x 10 Sq. mm | MTS | 88 | 330 | 29040
151 | End terminations | MTS | 4 | 550 | 2200
152 | 1 Core x 6Sq. mm including Terminations | MTS | 180 | 275 | 49500
153 | 1 Core x 4Sq. mm including Terminations | MTS | 150 | 220 | 33000
154 | Rubber mat 1100V grade ISI approved - 2 m x 1m | NOS | 1 | 4400 | 4400
155 | Shock treatment chart by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting in 3 languages (Telugu, English & Hindi) | NOS | 1 | 6050 | 6050
156 | First aid kit | NOS | 1 | 4400 | 4400
157 | Danger boards | NOS | 1 | 1320 | 1320
158 | Danger signage stickers on DB frames | NOS | 1 | 1320 | 1320
159 | Laminated Schematic with glass frame | NOS | 1 | 4400 | 4400
160 | Supply and Installation of DB Frame with wire ways shall be made out of 1.6mm thick CRCA sheet steel and powder coating colour shall match the colour of MCB DB's with hinged type door. 150mm x 100mm 1.6mm thick, wire ways / Raceway with 2mm thick screwed / press to fit cover with hinged type door for making Frame for MCB DB's. Complete required including installation accessories. | RMT | 15 | 3300 | 49500
161 | Supply, installation of powder coated MS box /angle support of 50x50x6mm size for suspending the lights below services and to route cable in same for connectivity with necessary accessories. ( Support for fixtures below AC duct) | NOS | 20 | 825 | 16500
162 | Supply, installation of powder coated 'C' channel support with thread rod support for suspending the lights below services and to route cable in same for connectivity with necessary accessories. ( Support for fixtures below AC duct) | NOS | 15 | 605 | 9075
163 | MS Fabricated Items | KG | 200 | 121 | 24200
164 | Temporary Lighting & Power arrangement with sufficient temporary Lighting ( Min 200Lux Ave. ) & power shall be provided to all agencies during execution with the following requirements | LS | 1 | 50000 | 50000

## UPS
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 80 KVA IGBT MODULAR UPS (N+1) | NOS | 1 | 1275000 | 1275000
2 | 20 KVA IGBT MODULAR UPS (N+1) | NOS | 1 | 390000 | 390000
3 | 6 KVA IGBT UPS (N+1) | NOS | 1 | 120000 | 120000
4 | 12V Batteries for 80KVA UPS with 15 Mins back-up | SET | 1 | 550000 | 550000
5 | 12V Batteries for 20 KVA UPS with 30 Mins back-up | SET | 1 | 280000 | 280000
6 | 12V Batteries for 6 kVA UPS with 30 Mins back-up | SET | 1 | 200000 | 200000
7 | Battery Racks - 80KVA, 15Mins | SET | 1 | 80000 | 80000
8 | Battery Racks - 20KVA, 15Mins | SET | 1 | 40000 | 40000
9 | Battery racks - 6 kVA, 30Mins | SET | 1 | 30000 | 30000
10 | Cu 1C x 16 sqmm flexible 5-Run - Sv-UPS Input (from MFP) | RMT | 75 | 275 | 20625
11 | Cu 1C x 16 sqmm flexible 5-Run - Sv-UPS Output to Sv-OP+STS Panel | RMT | 75 | 275 | 20625
12 | Cu 1C x 35 sqmm flexible 5-Run - WS-UPS Input (80 kVA, ~140A) | RMT | 75 | 650 | 48750
13 | Cu 1C x 35 sqmm flexible 5-Run - WS-UPS Output to WS-OP | RMT | 75 | 650 | 48750
14 | Cu 1C x 35 sqmm flexible 5-Run - STS Bus-Tie cable (WS-OP -> Sv-OP+STS) | RMT | 30 | 650 | 19500
15 | Cu 1C x 4 sqmm flexible 3-Run - Em-UPS Input + Output (1-ph) | RMT | 80 | 117 | 9360
16 | Cu 1C x 50 sqmm - Battery DC bus (Server UPS, +ve / -ve) | RMT | 50 | 750 | 37500
17 | Cu 1C x 70 sqmm - Battery DC bus (WS UPS, +ve / -ve) | RMT | 60 | 1030 | 61800
18 | Cu 1C x 10 sqmm - Battery DC bus (Em-UPS, +ve / -ve) | RMT | 20 | 200 | 4000
19 | Brass single-compression glands sized per cable (incl. shroud, washer) | LOT | 1 | 20000 | 20000
20 | Cu lugs, ferrules, heat-shrink, tags - all sizes | LOT | 1 | 25000 | 25000
21 | GI Duct 200x150 mm 24G - exhaust route to external riser | SQM | 6 | 2200 | 13200
22 | Pre-filter for fresh-air make-up + bird-mesh louver | LOT | 1 | 14500 | 14500

## HVAC_LOW SIDE
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Powder coated double skin plenum with all supports suiting to site conditions. Plenum colour shall be similar to the AHU.All supports to be consider with MS along with vibration arrestors & MS support painting to be consider along with primer. Plenum ,supports colour should match with AHU color | SQM | 60 | 660 | 39600
2 | 26 G Ducting with TDF flanges(0-750mm) | SQM | 240 | 66 | 15840
3 | 24 G Ducting with TDF flanges(751-1000mm) | SQM | 95 | 66 | 6270
4 | 22 G Ducting with TDF flanges(1001-1200mm) | SQM | 95 | 86 | 8170
5 | 20 G Ducting with TDF flanges(1201-2100mm) | SQM | 20 | 106 | 2120
6 | 18 G Ducting with TDF flanges(2100 & above) | SQM | 50 | 106 | 5300
7 | 24 G (0-600 mm) | SQM | 855 | 99 | 84645
8 | 22 G (601-1200mm) | SQM | 285 | 99 | 28215
9 | 20 G ( 1201 & above) | SQM | 285 | 132 | 37620
10 | 700 Cfm - 20 mm external static cabinet exhaust air fan with all necessary supports.(Cafe exhaust ) | NOS | 1 | 1980 | 1980
11 | 600 Cfm - 25 mm external static Cabinet type exhaust fan with all necessary supports. Battery exhaust with timer panel with nessarry supporting material | NOS | 1 | 1980 | 1980
12 | 350 x 350 MM (Neck Size) | NOS | 20 | 660 | 13200
13 | 300 x 300 MM (Neck Size) | NOS | 20 | 660 | 13200
14 | 225 x 225 MM (Neck Size) | NOS | 5 | 528 | 2640
15 | 3 slot, 20 mm slot (With Hit & miss collar dampers for Supply Air) | RMT | 30 | 198 | 5940
16 | 3 slot, 20 mm slot (Without collar dampers) | RMT | 125 | 198 | 24750
17 | 350mm dia | NOS | 20 | 264 | 5280
18 | 300mm dia | NOS | 6 | 264 | 1584
19 | Supply, testing, commissionig and balancing of Aluminium extruded powder coated square grilles with 4 side flanges and as per approved colour shade by the architect. 150 x 150 with collar damper | NOS | 35 | 264 | 9240
20 | Single/one way | SQM | 22 | 528 | 11616
21 | Single/one way | SQM | 20 | 528 | 10560
22 | Collar Dampers of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (quantity including for diffusers & grills) 24 guge should be considered.Qty is conisdered as per cross sectional area. Minimal quantities are not acceptable | SQM | 20 | 792 | 15840
23 | Volume Control Dampers made out of 100 x 40 x 1.2 mm thick galavanised steel frame and blades of 1.2 mm galavanised sheet steel with TDF flanges .Also suitable leavers for manual control and stickers/ engraving for open/ close identification should be consider post air balancing SMACNA standards to be followed for damper selection .Qty is considered with cross sectional area only.Minimum values are not accepted | SQM | 5 | 660 | 3300
24 | Elliptical Volume Control Dampers made out of 100 x 40 x 1.2 mm thick galavanised steel frame and blades of 1.2 mm galavanised sheet steel.Also suitable leavers for manual control and stickers/ engraving for open/ close identification should be consider post air balancing SMACNA standards to be followed for damper selection .Qty is considered with cross sectional area only.Minimum values are not accepted | SQM | 25 | 1056 | 26400
25 | Motorized Modulating type low leakage air dampers made out of 20 G Blade & Frame for fresh air modulation with actuator complete with all accessories like Actuator,control panel etc and any necessary requirement which can perform the controlling the Damper. It shall be integrated with Co2 sensor and based on CO2 levels, damper shall be modulate. | SQM | 13 | 1584 | 20592
26 | ACTUATORS with control panel | NOS | 18 | 660 | 11880
27 | 200 mm dia | RMT | 5 | 132 | 660
28 | 150 mm dia | RMT | 35 | 100 | 3500
29 | 200 mm dia | NOS | 10 | 66 | 660
30 | 250 mm dia | NOS | 40 | 66 | 2640
31 | 200mm dia | RMT | 10 | 66 | 660
32 | 250mm dia | RMT | 10 | 66 | 660
33 | Supply,installation,testing & comissioning of 525 x 525 x 400 mm High Sheet Metal Spill air boxes made out of 24 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.chain /link supports should be consider for all four corners of the diffuser & hook support to be provide at center of the mixing box to avoid resting on false ceiling | NOS | 19 | 660 | 12540
34 | Supply,installation,testing & comissioning of 1200 x 150 x 400 mm High Sheet Metal Spill air boxes made out of 24 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.chain /link supports should be consider for all four corners of the diffuser & hook support to be provide at center of the mixing box to avoid resting on false ceiling | NOS | 3 | 660 | 1980
35 | Supply,installation,testing & comissioning of 600 x 150 x 400 mm High Sheet Metal Spill air boxes made out of 24 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.chain /link supports should be consider for all four corners of the diffuser & hook support to be provide at center of the mixing box to avoid resting on false ceiling | NOS | 10 | 660 | 6600
36 | Supply,installation,testing & comissioning of 450 x 150 x 400 mm High Sheet Metal Spill air boxes made out of 24 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.chain /link supports should be consider for all four corners of the diffuser & hook support to be provide at center of the mixing box to avoid resting on false ceiling | NOS | 15 | 660 | 9900
37 | Firesealent for AHU Room,MDF,IDF,UPS& Battery rooms closure 3M /Hilti make passive fire protection material-( supply & return air ducts.) | SQM | 6 | 660 | 3960
38 | SITC of multibade Fire & smoke dampers CBRI Certified, Class 2 leakage with 120 minutus rating for AHU,firecompartment supply & return air ducts.16 Guage -frame & 16 Guage Blade to be considered. Sleeve length should be minimum of 500-600mm suituing to site conditions. Dampers should be procured post approval of shop dwgs .TDF Flange connection on both sides & space for installing the actuator should be considered on sleeve.The dampers shall be BMS compatible as per the specifications | SQM | 15 | 660 | 9900
39 | Supply ,installation, testing and commissioning of Spring return type 9NM Actuators for AHU room dampers complete as per technical specification & drawing details | NOS | 13 | 1584 | 20592
40 | Supply ,installation, testing and commissioning of Spring return type 4NM Actuators for AHU room dampers complete as per technical specification & drawing details | NOS | 5 | 1584 | 7920
41 | Supply ,installation, testing and commissioning of Fire damper control panel with maximum 4 outgoing feeders for Actuators and incomer from AHU starter panel, Control panel should have necessary provisions to take BMS contacts for each actuator status and also show local display with reset option. Necessary Terminal block to be provided for fire interlocking complete as per technical specification & drawing details | NOS | 1 | 3960 | 3960
42 | Supply ,installation, testing and commissioning of Individual Fire damper control panel for Actuators and incomer from AHU starter panel, Control panel should have necessary provisions to take BMS contacts for each actuator status and also show local display with reset option. Necessary Terminal block to be provided for fire interlocking complete as per technical specification & drawing details | NOS | 1 | 1980 | 1980
43 | Supply, installation, testing and commissioning of Fusible link type Fire Damper of 90 minutes fire resistant complete with all standard accessories. Fire damper as per CBRI Listed & certified, outer shell constructed with 1.6mm thick galvanized steel frame and the blade/Leaf with 1.6mm thick GSS in accordance with the GFC/ shop drawings Considered for store room supply & return air ducts & fire compartment crossing | SQM | 3 | 1980 | 5940
44 | Supply & Installation of 3CX2.5Sq.mmPVC insulated FRLS Multi strand copper conductor wire drawn in 20mm dia MS conduit form panel to damper | RMT | 150 | 13 | 1950
45 | Supply installation testing and commissioning of Back draft damper for all room dual units/source-18 Gauge with all necessary accessories | SQM | 1 | 132 | 132
46 | Supply & installation of the Fire Retardant double Canvas connection to the Ventilation ,AC units mouth should come zip arrangement. Vendor should check the unit in site and quote the same. Samples should be submitted before procuring the materials | SQM | 6 | 660 | 3960
47 | SITC of Fresh air cowl connection with bird screen and volume control dampers | SQM | 1.5 | 400 | 600
48 | 15mm thick | SQM | 275 | 132 | 36300
49 | 9 mm thick | SQM | 1550 | 132 | 204600
50 | AHU Room walls where ever indicated as per the drawings to be acoustically lined with 50 mm thick factory fabricated fibre glass glasswool acoustic panels of 1200 x 1200 mm or 600 x 600 mm in size. Air Gap of 50 mm to be provided behind the panels as shown in the drawings. Density shall be 48 kg/m3 and al. perforated sheet shall be of 24 G. Mockup to be done at site before executing at site for PMC/client/consulatnt approval | SQM | 100 | 66 | 6600
51 | Supply,Installation & commissioning | SQM | 20 | 792 | 15840
52 | Air balancing should be done for TWO times - Pre occupancy & Post occupancy along with clinet/PMC & Facility teams. All necessary tools(Anemo meter/ digital HOOD) should be consider in costing. Please refer AHU schedule for AHU capacities .Vendor to fix the hot spots. Air balancing random check during handover/ demo to facility team also needs to be done. Air balancing shall be done with hood meter only. % of tolerance to be mentioned. To be carried out for both supply & return air. Air balancing, fixing hot spots, setting up VFD/EC Hz level in starter panel, AHU filter side reading in cross matrix etc complete needs to be captured. Vendor to show DB level at 1mts away from AHU room wall. DB level should be 55dB at AHU room wall & 51± 2dB at 1M distance | LOT | 1 | 65000 | 65000
53 | Supply , installtion testing & comissioning of DP sensor with 500pa laong with the 19mm conduit and suitable cabling and supports | NOS | 1 | 2772 | 2772
54 | Supply , installtion testing & comissioning of return air temperature sensor along with 19mm conduit and suitable cabling and supports | NOS | 1 | 396 | 396
55 | Chipping, chassing & Plastering the wall openings in cement mortor 1:6 of 15 mm thick finishing to line and level with sand faced finshing at all levels, including all leads & lifts, scaffolding, curing etc complete (for Supply & Return air duct openings in ahu rooms etc) | SQM | 5 | 55 | 275
56 | Supply installation of chequered plate of 8mm thick ness for shaft closure with all necessary supports | SQM | 3 | 132 | 396
57 | SITC of Flameproof Hydrogen sensor (for battery room) Hydrogen Transmitter shall be wall mounted with 0-100% LEL Range & UL/CE listed. Sensing Technology should be PID and typical area coverage should be greater than 300 m2. Transmitter should have audio (Buzzer) and visual alarms when Hydrogen is detected.The accuracy for the transmitter should be ±0.5%. The transmitter should be able to operate from -10°C to 50°C. The enclosure should be explosion-proof, certified by CCOE / equivalent government body.The sensor should be calibrateable and rerangeable on site. | NOS | 1 | 10000 | 10000
58 | SITC of Duct Mounted explosion proof fan Suitable for use in Battery rooms. Fans should be powered by EX motors with Centrifugal Backward Curve impellers made out of powder-coated steel plate. The fans shall be compliant with the Essential Health and Safety Requirements and compliance with: Explosion proof version comply with EN 60079-0, EN 60079-7, EN 14986, DIN EN ISO 80079-36 and DIN EN ISO 80079-37. Local BMS compatible Control Panel for UPS / battery Room Exhaust fan with DOL Starter & 24Hrs Digital programmable timer & 24V Transformer with PLA Relays for Fire system & Hydrogen Sensor system to be included. 200cfm, 20mm ESP | NOS | 1 | 10000 | 10000

## HVAC_VAV
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply,installation,testing & commissioning of VAV boxes | NOS | 4 | 2592 | 10368
2 | Supply,installation,testing & commissioning of VAV boxes | NOS | 12 | 2592 | 31104
3 | Supply,installation,testing & commissioning of VAV boxes | NOS | 2 | 2592 | 5184
4 | Supply,installation,testing & commissioning of VAV boxes | NOS | 3 | 2592 | 7776
5 | Supply,installation,testing & commissioning of VAV boxes | NOS | 4 | 2592 | 10368
6 | Supply,installation,testing & commissioning of VAV boxes | NOS | 15 | 2592 | 38880
7 | Supply,installation,testing & commissioning of VAV boxes | NOS | 11 | 2592 | 28512
8 | Factory fabricated Z type Cross Talk Silencer Supply and Fixing of Cross Talk silencer fabricated using 22G GI Sheets with internal 15mm thick open cell nitrile rubber insulation. | NOS | 5 | 1000 | 5000
9 | Supply,installation,testing & comissioning of '2core, 1.5 Sqmm, screened ATC/sheathed cable communication cable in PVC Conduit of 19 mm dia for looping between VAV to VAV with all supports | RMT | 200 | 58 | 11600
10 | Supply,installation,testing & comissioning of 4Core 1Sqmm cable with all supports in PVC Conduit of 19 mm dia for VAV controller to thermostat etc.. | RMT | 750 | 58 | 43500
11 | Providing, fixing, testing & commissioning of back pressure DP sensors suitable for use with air having measurement range of 0-100 pascal with accuracy of +/-3% complete with 220/ 24 V transformer. | NOS | 2 | 1000 | 2000

## HVAC_VRF
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Outdoor Unit(ODU) : Cooling Capacity : 4 HP - CRITICAL AREAS - SIDE DISCHARGE | NOS | 4 | 8000 | 32000
2 | Outdoor Unit(ODU) : Cooling Capacity : 12 HP - CRITICAL AREAS - TOP DISCHARGE | NOS | 1 | 15000 | 15000
3 | HS/LS DUCTABLE - 2 TR | NOS | 3 | 5000 | 15000
4 | 4-WAY STD CASSETTE - 2 TR | NOS | 5 | 3500 | 17500
5 | Hi-wall - 2 TR | NOS | 2 | 2760 | 5520
6 | Hi-wall - 1 TR | NOS | 2 | 2760 | 5520
7 | 1.5 TR DX-STD CASSETTE | NOS | 1 | 3500 | 3500
8 | Supply of Wired / Wireless Remote controllers for indoor units | NOS | 12 | 300 | 3600
9 | 28.6mm OD (insulation = 19mm thick) | RMT | 30 | 216 | 6480
10 | 22.2mm OD (insulation = 19mm thick) | RMT | 10 | 216 | 2160
11 | 19.1mm OD (insulation = 19mm thick) | RMT | 10 | 216 | 2160
12 | 15.9mm OD (insulation = 19mm thick) | RMT | 210 | 216 | 45360
13 | 12.7mm OD (insulation = 19mm thick) | RMT | 30 | 216 | 6480
14 | 9.5mm OD (insulation = 19mm thick) | RMT | 10 | 216 | 2160
15 | 12.7mm OD (insulation = 13mm thick) | RMT | 80 | 216 | 17280
16 | 9.5mm OD (insulation = 13mm thick) | RMT | 210 | 216 | 45360
17 | 6.4mm OD (insulation = 13mm thick) | RMT | 40 | 216 | 8640
18 | 50 mm dia | RMT | 10 | 100 | 1000
19 | 40 mm dia | RMT | 40 | 90 | 3600
20 | 32 mm dia | RMT | 40 | 80 | 3200
21 | 25 mm dia | RMT | 30 | 72 | 2160
22 | Electrical Cable between Isolator to ODU.Suitable size copper flexible cable with necessary earthing insulation | RMT | 36 | 14 | 504
23 | Providing & fixing of 2 Cx 1.5 sqmm cu. cable for control cum trans-mission between Indoor unit and Out Door Unit through PVC Conduit. | RMT | 450 | 29 | 13050
24 | Imported fittings like Y-Joints and headers etc as per the layout( additional supports should consider for both ends of the Y joint) | NOS | 6 | 288 | 1728
25 | Filling, testing, commissioning including topping up of R410 A Refrigerant. | KG | 32 | 1200 | 38400
26 | Sequential Controller for AC unit to programme the run hours of compressor.For Server Room , UPS Room, Electrical, Hub Room & 24x7 Area | NOS | 3 | 2000 | 6000
27 | SITC of external Heavy duty type Drain pump kit with tank for CSU, Ductable and Hi wall split units to carry condensate drain. The pump should be capable to pump water upto 3M high. | NOS | 4 | 1000 | 4000
28 | Supply, Installation, Commissioining and Testing of necessary Three pin tops for VRV indoor units | NOS | 12 | 500 | 6000
29 | size:150x 50mm(14 SWG grade)-2mm thick | RMT | 50 | 43 | 2150
30 | size:300x 100mm with cover (14 SWG grade)-2mm thick Only for Exposed & Vertical shaft area | RMT | 20 | 43 | 860

## Passive Networking
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Cat6A UTP cable Box of 305 Mtrs 23Awg LSZH | BOX | 182 | 18000 | 3276000
2 | Cat6A Information Outlet - Active Data - Blue | NOS | 425 | 380 | 161500
3 | Cat6A Information Outlet - Redundant Data- Yellow | NOS | 366 | 380 | 139080
4 | 24 Port Jack Panel Angled - Unloaded | NOS | 33 | 7000 | 231000
5 | Cat6APatch cord -2 meters for Active Data - Blue | NOS | 298 | 380 | 113240
6 | Cat6APatch cord -3 meters Active Data - Blue | NOS | 128 | 490 | 62720
7 | Cat6APatch cord -2 meters Redundant Data - Yellow | NOS | 92 | 380 | 34960
8 | Cat6A Information Outlet - Active Data - Blue | NOS | 425 | 380 | 161500
9 | Cat6A Information Outlet - Redundant Data- Yellow | NOS | 366 | 380 | 139080
10 | Face Plate, 2 Port (White) | NOS | 434 | 160 | 69440
11 | Cat6A Patch cord -2 meters for Active Data - Blue | NOS | 425 | 380 | 161500
12 | Cat6A UTP cable Box of 305 Mtrs | NOS | 6 | 18000 | 108000
13 | Cat6A Information Outlet - WIFI | NOS | 10 | 380 | 3800
14 | 24 Port Jack Panel Angled - Unloaded | NOS | 1 | 7200 | 7200
15 | Cat6A Patch cord -3 meters for WIFI both sides | NOS | 10 | 490 | 4900
16 | 6-Core Fiber OM4 Fiber cable | MTRS | 180 | 120 | 21600
17 | 24Fiber OM4 Fiber panel loaded with LC adaptors & Pigtails | NOS | 4 | 18000 | 72000
18 | 48Fiber OM4 Fiber panel loaded with LC adaptors & Pigtails | NOS | 2 | 28000 | 56000
19 | Fiber Patch cord Duplex LC-LC - 3 meters | NOS | 48 | 700 | 33600
20 | Fiber Patch cord Duplex LC-LC - 5 meters | NOS | 24 | 950 | 22800
21 | 42U - 800X1000MM Closed Rack with all Standard accessories | NOS | 2 | 70000 | 140000
22 | 24 U - 550X500MM Closed Rack with all Standard accessories | NOS | 2 | 28000 | 56000
23 | Horz. Cable Organiser/2U/Channel On Front | NOS | 8 | 1200 | 9600
24 | High Density Vertical Cable Organiser/12 inch/Front &Back/42U/Black | NOS | 4 | 7500 | 30000
25 | High Density Vertical Cable Organiser/8 inch/Front &Back/42U/Black | NOS | 4 | 6500 | 26000
26 | Run-Way Kit-20Inch/Black | NOS | 4 | 7000 | 28000
27 | Mounting Hardware/OR/Pk-20 | NOS | 120 | 300 | 36000
28 | PDU Brackets for mounting the Vertical PDU | NOS | 8 | 900 | 7200
29 | Ladder water fall kit | NOS | 4 | 2400 | 9600
30 | Server /IT Rack mount power distribution unit, 1Ph, 230V, 32A, 50/60Hz, Zero U standard with 12 X Indian Round Pin 5/15A, 16A MCB X 2 Circuits- PDU Rating 7.3KVA/Bottom feed-3Mt/ Black/ Inlet Plug Not Installed (32 Power Sockets) | NOS | 2 | 25000 | 50000
31 | Server /IT Rack mount power distribution unit, 1Ph, 230V, 32A, 50/60Hz, Zero U standard with 12 X Indian Round Pin 5/15A, 16A MCB X 2 Circuits- PDU Rating 7.3KVA/Bottom feed-3Mt/ Black/ Inlet Plug Not Installed | NOS | 4 | 25000 | 100000
32 | Patchcord Labels | LS | 1 | 10000 | 10000
33 | Consumables | LS | 1 | 5000 | 5000
34 | WIFI Stand | NOS | 10 | 800 | 8000
35 | CCTV Pole wite Round clamp | NOS | 25 | 1500 | 37500
36 | UTP cable laying Bunching dressing termination Jack panel mounting faceplate termination | Per node | 801 | 300 | 240300
37 | Fluke Testing - UTP testing and scanning | NOS | 801 | 120 | 96120
38 | Labelling - Jack panel & Faceplate | NOS | 801 | 40 | 32040
39 | Rack Mounting and installation | NOS | 3 | 5000 | 15000
40 | Access point mounting which is supplied by customer | NOS | 10 | 500 | 5000
41 | CCTV Pole and WIFI Poles installation | NOS | 35 | 400 | 14000
42 | On Site Coordination, Project Management, As built Docs & warranty ,WCP & CAR policy | LS | 1 | 50000 | 50000

## Networking - Nodes
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Workstation | 305 | 1 | 1 | 1
2 | Cabin | 6 | 1 | 1 | 1
3 | 4 Pax Meeting Room | 6 | 1 | 1 | 1
4 | 4 Pax Meeting Room AV/TV | 6 | 2 | 1 | 2
5 | 6 Pax Meeting Room | 1 | 1 | 1 | 1
6 | 6 Pax Meeting Room AV/TV | 1 | 2 | 1 | 2
7 | 8 Pax Meeting Room | 1 | 2 | 2 | 4
8 | 8 Pax Meeting Room AV/TV | 1 | 2 | 1 | 2
9 | 12 Pax Meeting Room | 1 | 4 | 4 | 16
10 | 12 Pax Meeting Room AV/TV | 1 | 2 | 1 | 2
11 | 20 Pax Broad Room | 1 | 4 | 4 | 16
12 | 20 Pax Broad Room AV/TV | 2 | 4 | 2 | 8
13 | Cafeteria - 47 PAX | 1 | 2 | 2 | 4
14 | Cafeteria - 47 PAX AV/TV | 1 | 2 | 1 | 2
15 | Server room | 1 | 1 | 1 | 1
16 | UPS and Electrical Room | 1 | 1 | 1 | 1
17 | Battery Room | 1 | 1 | 1 | 1
18 | Collab/Breakout Area | 3 | 1 | 1 | 1
19 | Collab/Breakout Area AV/TV | 3 | 2 | 1 | 2
20 | Reception + Waiting Area | 1 | 2 | 2 | 4
21 | Reception + Waiting Area AV/TV | 1 | 2 | 1 | 2
22 | Buffer | 10 | 1 | 1 | 1
23 | Repro | 8 | 1 | 1 | 1
24 | WIFI approx | 10 | 1 | 1 | 1

## Fire & Security
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 25 NB | MTRS | 350 | 90 | 31500
2 | 32 NB | MTRS | 48 | 90 | 4320
3 | 40 NB | MTRS | 58 | 90 | 5220
4 | 50 NB | MTRS | 75 | 90 | 6750
5 | 65 NB | MTRS | 50 | 90 | 4500
6 | 80 NB | MTRS | 53 | 90 | 4770
7 | 100 NB | MTRS | 120 | 90 | 10800
8 | 150 NB | MTRS | 28 | 90 | 2520
9 | 10 mm Bullet Fastner | NOS | 125 | 21 | 2625
10 | GI U-Clamp | NOS | 125 | 29 | 3625
11 | 10 mm GI threaded stud rod | MTRS | 125 | 26 | 3250
12 | Supply Installation testing & comissioning of Concealed type, Bulb type sprinkler with Fusible coverplate of 15 NB, 68 deg.with heat activated, Standard Response, powder coated plate | NOS | 18 | 302 | 5436
13 | Supply Installation testing & comissioning of Pendant type sprinkler of 15 NB, Quartzoid bulb type 68 deg.Quick Response, with adjustable escutcheon plate in SS 304. | NOS | 222 | 155 | 34410
14 | Supply Installation testing & comissioning of Upright type sprinkler of 15 NB, Quartzoid bulb type 68 deg, Quick Response, with SS 304 sprinkler guard if required. | NOS | 20 | 204 | 4080
15 | - Size 150 NB. | NOS | 4 | 1388 | 5552
16 | 1500 mm long | NOS | 65 | 564 | 36660
17 | Providing and fixing of Sprinkler Hard drop pipes made of 25 NB GI Pipe with socket weld fittings with welded reducer on one end to directly accommodate sprinkler with supports (Length up to 2.5 Mtrs). | NOS | 40 | 400 | 16000
18 | 150 NB | NOS | 4 | 5227 | 20908
19 | 150 NB | NOS | 4 | 3022 | 12088
20 | Providing and fixing 50 mm dia Gate valve as per IS 778 for sprinkler drain with Tamper switch, On/Off status shall be monitored by BMS System. | NOS | 4 | 1878 | 7512
21 | Providing and fixing 50 mm dia Ball valve, As per BS 5351, Listed type, ISI Marked. | NOS | 4 | 898 | 3592
22 | Providing and fixing 25 mm Test Valve Drain kit with sight Glass, Ball valve, Union & required fittings etc | NOS | 4 | 1388 | 5552
23 | SITC of 25mm dia Air Vent Valves at Sprinkler Tapoffs with Ball Valve. | NOS | 4 | 531 | 2124
24 | SITC of Pressure Guage 0 - 10 Kg / cm2, glycerin filled with mounting arrangement and ball valve. | NOS | 4 | 466 | 1864
25 | 150 NB | NOS | 4 | 4573 | 18292
26 | Supply & Installation of Powder Coated Rosette Plates for fixing the pendant sprinklers to the false ceiling. | NOS | 80 | 57 | 4560
27 | Pressure testing and commissioning of sprinkler pipe with 12 bar pressure both side to be hold for 24 Hours | LOT | 2 | 5717 | 11434
28 | FORM A required for Sprinkler work.(Fire Vendor have to MC Fire lincence holder only.) | LOT | 1 | 50000 | 50000
29 | Drencher Open-Spray Nozzle - brass / chrome, K-115, NFPA 13 deluge type.1/2" NPT, K-115 | NOS | 85 | 270 | 22950
30 | GI Sch-40 pipe - 100 mm NB drencher header.100 mm NB | MTRS | 210 | 300 | 63000
31 | Drencher Deluge Valve Set - hydraulic / electrical release, with trim & tamper, actuated by FA Loop Control Module.100 mm | SET | 2 | 30217 | 60434
32 | Solenoid Valve for Deluge release - brass, 24V DC, NC.1/2" 24V DC | NOS | 1 | 1388 | 1388
33 | Drencher pipe fittings + supports.as required | LOT | 1 | 2450 | 2450
34 | Pressure switch for drencher line monitoring - to FA Monitor Module.0-16 bar | NOS | 1 | 1225 | 1225
35 | Supply & Installation Testing ,commissioning of, Addressable Main Fire Alarm complete as per UL Listed Addressable Fire Alarm Panel,Supply, Installation, Testing & Commissioning of Analog Addressable Fire Alarm Control panel . The Fire Alarm Control Panel(2 loop) shall include a full featured operator interface control and annunciation panel that shall include a backlit liquid crystal display, individual, color coded system status LEDs minimum 4 access levels, flash E-PROM. Each loop shall be loaded with 80% devices of manufacturer specified capacity , cable length being restricted to 80% of manufacturer specified maximum loop length and device capacity. The control panel shall be capable of expansion up to 4 loops with BMS Connectivity over Bacnet/IP. The system shall be capable of annunciation . The panel shall be UL Listed & FM Approved. The Price shall include Batteries with Battery charger housed in a wall mount enclosure. The system shall support control and supervision of connected devices. | SET | 1 | 25000 | 25000
36 | Addressable type Heat Detector with with muiltiple algorithms setting Base & MS Powder coated Junction Box for Above Ceiling and Below cieling. The detectors shall be UL Listed & FM Approved. | NOS | 2 | 350 | 700
37 | Addressable type Optical Smoke Detector with with muiltiple algorithms setting Base & MS Powder coated Junction Box for Above Ceiling . The detectors shall be UL Listed & FM Approved. | NOS | 42 | 350 | 14700
38 | Addressable type Optical Smoke Detector with with muiltiple algorithms setting Base & Below cieling. The detectors shall be UL Listed & FM Approved. | NOS | 103 | 350 | 36050
39 | Addressable type MUILTISENSOR (smoke & heat) detector with to distinguish and differenciate between real fire, steam and dust to avoid any false alarm with muiltiple algorithms setting with base & MS Powder coated Junction Box. The detectors shall be UL Listed & FM Approved. | NOS | 5 | 350 | 1750
40 | Isolator Base Module to be placed strategically between every 20 detectors for Loop isolation.The device shall be UL Listed & FM Approved. | NOS | 8 | 350 | 2800
41 | Remote response indicator having twin LED flush mounted on false ceiling/wall as per IS 2189 | NOS | 42 | 100 | 4200
42 | Addressable Dual Action Manual Pull station with Reset Lock & Key arrangment with back box and SS brushed steel Front plate of min. 1mm thick.The device shall be UL Listed & FM Approved. | NOS | 7 | 400 | 2800
43 | Hooter/Sounder cum Strobe / Flasher | NOS | 7 | 400 | 2800
44 | Control/Monitor/Relay/IO ModLPCBes with in built Isolators in suitable ABS Plastic glossy Box with SS brushed steel Front plate of 1 mm thick. The devices shall be UL Listed & FM Approved. | NOS | 18 | 400 | 7200
45 | SITC of 2 Core x 1.5 mm2, Multistranded AT Copper, FRLS, Armoured cable confirming to IS Standards, RED in Colour. The cable shall be laid on surface with GI saddle-spacers every 0.3 meters. Complete with GI Junction Box, lugs, cable compression glands, cable tags and Ferruling. | MTRS | 2670 | 40 | 106800
46 | GI Perforated Cable trays -50x 25 | MTRS | 30 | 50 | 1500
47 | Ceiling speakers - 6 Watts output with multiple tappings- EN 54 Approved with metal backbox | NOS | 105 | 200 | 21000
48 | 6 Zone Call Station with goose neck Microphone with zone selection & all call selection to be connected peer to peer with the network controller. | NOS | 1 | 5000 | 5000
49 | Master controller - 6 zone with following features- EN 54 Approved8 ZONE VOICE ALARM CONTROLLER | NOS | 1 | 30000 | 30000
50 | 480W Class D Power Amplifier fully monitored speaker circuits MUILTI Channel + One redundant suitable to meet the speaker wattage as per final DBR with 230 VAC networkable with all interconnecting Cables - EN 54 | NOS | 1 | 20000 | 20000
51 | 27U | NOS | 1 | 3000 | 3000
52 | 2C x 1.0 mm2, Stranded Copper conductor, Type AST 1 PVC insulated, Armoured ZHFR Cable 650 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands, ABS Junction Boxes (wherever required), terminals, Ferruling complete. | MTRS | 1390 | 30 | 41700
53 | GI Perforated Cable trays -50x 25 | MTRS | 20 | 100 | 2000
54 | Powder Coated 18 Gauge Truncking - 200 x 50 | MTRS | 20 | 100 | 2000
55 | ISI mark 4.5 KG CO2 SS Body fire Extingusher with wall mounting bracket. | NOS | 5 | 400 | 2000
56 | ISI Marked 6 Kg ABC Type SS Body fire Extingusher with MAP 90% with wall mounting bracket. | NOS | 19 | 400 | 7600
57 | 15 KG Ceiling Suspended Modular Type SS Body Clean Agent Fire Extinguisher | NOS | 1 | 7500 | 7500
58 | 10 KG Ceiling Suspended Modular Type SS Body Clean Agent Fire Extinguisher | NOS | 6 | 5000 | 30000
59 | Floor Mount MS Stands for the above extinguishers | NOS | 24 | 100 | 2400
60 | Main Rodent Controller with LCD Display, suitable to connect 25 satellites in Dedicated Connection with Dedicated Drivers with 5 Ultrasonic Frequency Bands with RS 485 Serial Connection. Looping of Satelittes is not permitted. | SET | 1 | 4000 | 4000
61 | Satellite Stations / Transducers covering 500 sq ft.area in all the voids. | NOS | 13 | 200 | 2600
62 | 2C x 14/40 SWG Copper Cable in below Conduit | MTRS | 180 | 30 | 5400
63 | Supply & Laying of 25 mm, 1.6 mm thick rigid GI conduits.Rate shall include wall chasing & rough plastering, clamping / fixing arrangement. | MTRS | 120 | 20 | 2400
64 | Bracket for Mounting the Rodent Panel | SET | 1 | 300 | 300
65 | Supply, installation, testing and commissioning of digital microprocessor- based ultrasonic controlled main panel/controller, wall mounting type with facility to connect up to 24 transducers. The operating frequency shall be > 20kHz and < 60kHz. The front fascia shall have a LCD display and on board controls to change, view and operate the menu. The panel/controller shall be complete in all respects as specified in the technical specifications.THE RRS PANEL WITH RS 485 BMS COMPATIBLE FOR INTEGRATION TO BMS SYSTEM | LOT | 2 | 1216 | 2432
66 | Electronic Hooter cum flasher for water sensing indication. | NOS | 2 | 608 | 1216
67 | Supply, installation, testing and commissioning of Water leak sensing cable twisted of 15 mts. long, mechanically strong, resistant to corrosion and abrasion. The cable shall be constructed with two sensing wires,an alarm signaling wire and an continuity wire and all shall be in a fluoropolymer carrier ( OR equi. material).The cable shall have factory installed connectors that can help to plug other cable together for extension.The cable shall be rugged in construction, no metal exposes, enables it to be reusable even in corrosive environment.Quoted price shall inclusive of all fixing accessories, end caps and probes (if required). | MTRS | 45 | 48 | 2160
68 | Supplying,laying, terminating, testing & commissioning of FRLS insulated, sheathed copper conductor, Shielded, armoured cables, Twisted pair, 2C x 1.5 sq.mm cable with ISI Certified, as per the relavent IS standards and specifications with all necessary termination accessories as required. The quoted rate shall be inclusive of suitable saddles, hardware, junction boxes etc. complete. | MTRS | 65 | 30 | 1950
69 | SURFACE MOUNT SINGLE SIDED, Maintained 3 Watt LED, FIRE Exit luminaires, with Sheet metal Body, Painted to RAL 9010, Pictogram 280 (I) X 130 (W), Legend with clear acrylic/engraved pattern to be fully compliant with requirements of designing and installation to meet the fire and safety code of practice, IP 20 with NiCad 2 x 1.2V Battery Backup for 90 Minutes with operation in following formats as per Layouts : Right Arrow, Left Arrow, Down Arrow, Both sides etc. Input Supply : 220 V AC ±10% | NOS | 4 | 500 | 2000
70 | FLUSH MOUNT DUAL SIDED, Maintained 3 Watt LED, FIRE Exit luminaires, with Sheet metal Body, Painted to RAL 9010, Pictogram 280 (I) X 130 (W), with spring supports, Legend with clear acrylic / engraved pattern to be fully compliant with requirements of designing and installation to meet the fire and safety code of practice, IP 20 with NiCad 2 x 1.2 V Battery Backup for 90 Minutes with operation in following formats as per Layouts : Right Arrow, Left Arrow, Down Arrow, Both sides etc. Input Supply : 220 V AC ±10% | NOS | 10 | 500 | 5000
71 | A2 Size Fire Evacuation Maps with Acrylic sheet & necessary fitting for wall mounting. | NOS | 6 | 500 | 3000
72 | Fire Extinguisher Signages | NOS | 31 | 50 | 1550
73 | Supply and installation of Smart Card reader with read range of 3 to 4 inches (HID Compatible Readers) | NOS | 9 | 1000 | 9000
74 | 2 DOOR | SET | 3 | 3000 | 9000
75 | Cabinets for above door controllers with 60W power supply | NOS | 4 | 750 | 3000
76 | Single Magnetic Lock with Door Position Switch | NOS | 6 | 300 | 1800
77 | Egress Switch | NOS | 6 | 100 | 600
78 | Magnetic contacts and Piezo Sounders for Fire Exits | NOS | 1 | 300 | 300
79 | Panic Bar with Hooters for all Emergency Exits / Local scare Alarm | NOS | 1 | 1000 | 1000
80 | Enterprise Access Control Software with 2 Client License loaded on Intel Xeon Server grade machine with 4 GB RAM & 240 GB Hardisk,with MS SQL Licensed Software & Operating System with following features: (Hardware in Client's Scope)- iApp Integrated Application | NOS | 1 | 10000 | 10000
81 | Controller to Reader Cabling - 8C X 20AWG | MTRS | 650 | 20 | 13000
82 | Controller to EM Lock Cabling - 4C X 20AWG | MTRS | 600 | 20 | 12000
83 | Controller to Switch/Controller Cabling - 2C x 20AWG | MTRS | 300 | 20 | 6000
84 | Supply & Laying of 25 mm, 1.6 mm thick rigid GI conduits.Rate shall include wall chasing & rough plastering, clamping / fixing arrangement. | MTRS | 300 | 30 | 9000
85 | Supply installation, testing, commissioning of Green ABS plastic Emergency Break Glass Units. | NOS | 5 | 200 | 1000
86 | Manual Key Switch | NOS | 3 | 200 | 600
87 | EM RFID Cards suitable to work with installed readers. | NOS | 240 | 40 | 9600
88 | Supply Installation, Testing and comissioning of 32 Channel Netwrok Video Recorder Embedded OS Linux CPU ARM Processor Flash 256 MB RAM 2 GB Watchdog Hardware + Software Power Restoration System Restart Automatically after Power Recovery HDD Devices Internal x 4 HDD Max. (Total 16 TB HDD required ) Capacity 4 TB x 4 Disk Management Create, Format and Remove Disk HDD S.M.A.R.T Video Output HDMI x 1, VGA x 1 Resolution 1920x1080, 1280x720 Graphics Decoder Hardware decoding H.265/H.264: 2560x1920 @ 30 fps (1-CH) 1920x1080 @ 120 fps (4-CH) 1280x720 @ 240 fps (8-CH) 1280x720 @ 480 fps (16-CH) 720x480 @ 960 fps (32-CH) USB Interface Front: 2 (USB 2.0) Back : 1 (USB 3.0) Alarm In 8 Alarm Out 4 Audio 3.5 Phone Jack Audio Output x 1 3.5 Phone Jack Audio Input (Reserved) x 1 RS485 1 Port (Reserved) Network Interface 10/100/1000Mbps Ethernet (RJ-45) x 2 Protocols IPv4, TCP/IP, HTTP, HTTPS, UPnP, RTSP/RTP/RTCP, SMTP, FTP, DHCP, NTP, DNS, DDNS, IP Filter Power Safety Certifications CE, LVD, FCC, VCCI, UL Listed, ONVIF Complaint, as per detailed specifications.RAID5 configured Calculated @ H.264 Compression, 25 fps @ 720p, 60 days, 12 hrs of Motion Based recording. Bidders to Provide Storage Calculations to substantiate the Storage Requirements in the Tender. If a Bidder would require larger storage, the same to be mentioned and included in this line item.The storage shall be min 30 days | NOS | 1 | 10000 | 10000
89 | Supply, Installation, Testing and Commissioning of Fixed Dome 1/2.8" Progressive CMOS 4 MP Indoor 1920x1080 VF f = 2.8-6mm, POE. Field of View 109° (Horizontal) 61° (Vertical) 126° (Diagonal) With Built-in IR illuminators, effective up to 30 meters with Smart IR, IR LED*2 SNV Min. Illumination 0.07 Lux @ F1.6 (Color) 0.001 Lux @ F1.6 (B/W) 0 Lux with IR illumination on 3D Noise Reduction. Should have 120 dB WDR MicroSD/SDHC/SDXC card slot Approvals required : CE, LVD, FCC Class B, VCCI, C-Tick, UL, Complete with required accessories, patch cords, convertors, Ajustable stand for mounting the cameras in open office areas, etc. | NOS | 25 | 600 | 15000
90 | Monitor 32" high perfomance TFT Multi mode LCD, VGA, 2 looping composite, S-video & DVI input, USB Hub,100-230 VAC 50 Hz | NOS | 1 | 3000 | 3000
91 | RJ 45 Connectors | SET | 40 | 30 | 1200
92 | Supply Installation, Testing and comissioning of 16 port layer 2 switch with 10/100/1000 POE Managed Switches with IP multicast snooping and data-driven IGMP support and with two 1000baseT single mode FO uplink ports and all related termination accessories as per site specific System requirement. Complete with 9u rack | NOS | 2 | 5000 | 10000

## GSS
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Seamless Cylinder CCOE Approved, complete with valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure, a pressure gauge with a safety burst disc and a safety Cap as per the technical specifications with all accessories complete as required 80 LTRS | NOS | 1 | 110000 | 110000
2 | FK-5-1-12 Gas as per the technical specifications. | KG | 60 | 2090 | 125400
3 | Complete Primary Kit for Master cylinder- Solenoid Valve, Pr. Guage , Manual- Pneumatic Actuator, Flexible Discharge & Actuation tube / Hose, Elbow & male connector as reqd, Warning sign and other items as required and as per the technical specifications with all accessories as required. | NOS | 1 | 55000 | 55000
4 | Discharge Nozzles are designed to provide the proper flow rate and distribution of NOVEC 1230 to total flood a hazard area: 360 deg. as per the technical specifications with all accessories as required. | NOS | 4 | 3900 | 15600
5 | Cylinder strap with a rail and hardware as per the technical specifications with all accessories as required.( Fabricated) | NOS | 2 | 14000 | 28000
6 | Hooter cum Strobe and warning Display board outside the room as per the technical specifications with all accessories as required. | SET | 2 | 2922 | 5844
7 | Piping, fittings & supports, etc.ASTM Grade A Sch. 40 as per the technical specifications with all accessories as required.(MSL/JINDAL) | LOT | 1 | 66000 | 66000
8 | Manual Abort and Release station in Break glass enclosure as per the technical specifications with all accessories as required. | SET | 1 | 2686 | 2686
9 | Conventional 2 zone Gas Release Panel | NOS | 1 | 12486 | 12486
10 | Conventional Smoke detectors | NOS | 6 | 1774 | 10644
11 | Response Indicators for above somke detectors | NOS | 4 | 223 | 892
12 | 2 Core 1.5 Sqmm Copper Armoured Cable as per the technical specifications with all accessories as required.(POLYCAB) | MTRS | 120 | 120 | 14400
13 | UL approved Flow calculation with piping isometric,Gas quantity,layout drawings, with Cylinder CCOE certificate for Storage cylinders,OEM fill certificate,Certificate for filling in India and all related documentation complete | Lot | 1 | 30000 | 30000
14 | Conducting Room Integrity Test : Door Fan test to meet the Requirements of the NFPA 2001, and predicting the efficacy of the Protected Area Enclosure from the perspective of Fire Suppression. | Lot | 1 | 67500 | 67500
15 | Installation, commissioning, testing and training | Lot | 1 | 65000 | 65000

## TOILET WORKS
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 150mm Thik AAC Block Wall | SQM | 192 | 1750 | 336000
2 | 100mm Thick Ledge Wall - 1200mm Height | SQM | 28 | 1550 | 43400
3 | Cement Plastering | SQM | 354 | 480 | 169920
4 | RCC Lintel (for Doors) | RMT | 6.5 | 2143 | 13929.5
5 | Waterproofing (For Floor + Walls 600 mm High) | SQM | 130 | 1050 | 136500
6 | Pest Control and Anti-Termite Treatment | SQM | 105 | 75 | 7875
7 | Printed Tile - Type -05 (Size: 600mm X 600mm) | SQM | 105 | 2015 | 211575
8 | Tile Cladding | SQM | 290 | 2000 | 580000
9 | BBC Raised Flooring - 300mm Height | SQM | 105 | 1400 | 147000
10 | Metal Modular perforated - Grid Ceiling - Waterproof :- | SQM | 105 | 1950 | 204750
11 | Mirror Panelling | SQM | 20 | 4500 | 90000
12 | TOILET CUBICLES - 1475MM(L) X 1000MM(W) | NOS | 16 | 23000 | 368000
13 | Restroom Signages - 300mm x 100mm | NOS | 6 | 450 | 2700
14 | Indoor strip light, 5Watts/Mtr, 5Mtr Reel , 24V DC, 3SDCM - PRIME WITH Surface Mount Aluminum Profile W: 16mm X H: 18mm Standard length -3 meter and 5 Nos Electronic Driver | RMT | 30 | 450 | 13500
15 | Supply, installation, testing and commissioning of ceiling-recessed LED downlight, complete with electronic ballast/driver, housing, clamps, and accessories for proper fixing. | NOS | 63 | 950 | 59850
16 | Granite jamb & soffit for door opening - 200mm to 250mm deep | RMT | 38 | 1350 | 51300
17 | Granite on counters | RMT | 8 | 9500 | 76000
18 | Full Height Storages (800mm x 450 mm x 2100mm) | NOS | 2 | 24500 | 49000
19 | Professional Deep Cleaning | LS | 1 | 35000 | 35000
20 | Regular Housekeeping During Project Execution, Debris Removal | LS | 1 | 55000 | 55000
21 | Providing and fixing white glazed vitreous china under-counter wash basin, installed below counter slab, complete with required cut-out in counter, including chrome plated brass waste coupling, fixing brackets, sealing with silicone, connection to inlet and outlet pipes, and making good all finishes, complete as required. Includes connection to plumbing lines and alignment as per approved layout; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 15 | 7054 | 105810
22 | Supply and installation of rimless wall-hung WC with UF soft-close seat cover and concealed fixing system. Includes all accessories, connection to drainage system, and proper alignment; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 17000 | 306000
23 | Supply and installation of wall-mounted urinal complete with fixing brackets and accessories. Includes connection to water inlet and drainage system; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 8 | 10500 | 84000
24 | Supply and fixing of stainless steel toilet roll holder with concealed mounting arrangement. Includes all hardware, fasteners, and installation complete; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 1845 | 33210
25 | Supply and installation of double robe hook in stainless steel finish with concealed fixing. Complete with all mounting accessories and installation; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 690 | 12420
26 | Supply and installation of health faucet set including 8 mm dia flexible hose, handset, and wall bracket. Complete with connection to water supply and all accessories; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 1845 | 33210
27 | Supply and installation of 32 mm click-clack waste coupling with full thread for wash basin. Includes proper sealing, fixing, and connection to waste line; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 15 | 1484 | 22260
28 | Supply and installation of 32 mm bottle trap with internal partition in chrome finish. Includes connection to basin outlet and waste line with all fittings; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 15 | 2205 | 33075
29 | Supply and installation of angular stop cock with wall flange in chrome finish. Includes connection to water supply line and proper fixing; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 1359 | 24462
30 | Supply and fixing of dual flush control plate compatible with concealed cistern system. Includes installation, alignment, and testing for proper operation; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 3679 | 66222
31 | Supply and installation of slim concealed cistern with complete internal mechanism and accessories. Includes flushing system, mounting frame, and connection to plumbing lines; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 18 | 6650 | 119700
32 | Supply and installation of sensor-based tall boy faucet for wash basin with IR sensor technology. Includes power supply, control unit, and all connections; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 15 | 7600 | 114000
33 | Supply and installation of concealed box for housing urinal sensor mechanism within wall. Includes fixing, alignment, and provision for electrical and plumbing connections; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 8 | 4180 | 33440
34 | Supply and installation of exposed sensor kit including sensor plate and control components. Complete with testing, commissioning, and integration with concealed system; Make: Jaquar/Kohler/Euronics or equivalent. | NOS | 8 | 6175 | 49400
35 | Urinal Pre laminated Solid Partition (Size -450mm x 1000mm) Providing & fixing Urinal Solid Partition of size 450 mm (W) × 1000 mm (H) fabricated using 12 mm thick Pre-laminated ply with as aprd., securely fixed to wall using SS 304 grade brackets / patch fittings, complete in all respects as per approved drawings and Architect’s specifications. Make :Jaquar/Kohler /Euronics equivalent | NOS | 8 | 12540 | 100320
36 | Supply, Installing & testing 15mm hot & cold wall Mixer along with spout with overhead shower with shower arm including CP flanges necessary fixing materials etc., complete. The flow rate of fixture shall be as per IGBC requirement. Make :Jaquar/Kohler /Euronics equivalent | NOS | 2 | 12350 | 24700
37 | Supplying, Fixing Towel Rail fixed with SS screws on to the Shower area. Make :Jaquar/Kohler /Euronics equivalent | NOS | 2 | 1934 | 3868
38 | Supply, Installing, testing and commissioning of 15 mm dia CP Angle cocks (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning)complete. Make :Jaquar/Kohler /Euronics equivalent | NOS | 4 | 1986 | 7944
39 | Providing, fixing and commissioning of liquid automatic soap dispenser near pantry, sensor-based touch-free operation, chrome finish body, including cutting, drilling and making good of walls, complete with all necessary fittings, accessories and AC power connection, installed as per manufacturer’s specifications and standards. Make :Jaquar/Kohler /Euronics equivalent | NOS | 6 | 6218 | 37308
40 | Supply and fixing of Stainless steel body paper towel dispenser with SS screws on the wall Make :Jaquar/Kohler /Euronics equivalent | NOS | 6 | 3325 | 19950
41 | Hand Dryer (Touch-Free Infrared – Wall Mounted) – Jaquar Nuovo Dual Flow / Euronics Jet or Equivalent Supply, installation, testing and commissioning of touch-free infrared sensor-operated hand dryer (Jaquar Nuovo Dual Flow / Euronics Jet or approved equivalent), suitable for wall mounting, with high-speed drying mechanism and hygienic operation. Unit to be complete with built-in sensor, motor, air filtration system, and all necessary mounting accessories, electrical connections, testing, commissioning, and handover as per manufacturer specifications. | NOS | 6 | 14725 | 88350
42 | Providing and fixing of the 15 mm dia brass bib cock with wall flange of following make. (or equal approved) Make :Jaquar/Kohler /Euronics equivalent | NOS | 4 | 2926 | 11704
43 | Capacity : 25 litre | NOS | 2 | 12540 | 25080
44 | WALL MOUNTED BASIN WITH FIXING ACCESSORIES - Handicap Washroom Make :Jaquar/Kohler /Euronics equivalent | NOS | 2 | 8883 | 17766
45 | Providing, fixing and commissioning of sanitary pad disposal bin for female washroom, wall-mounted unit made of durable material, suitable for hygienic disposal, including fixing arrangements, cutting and making good of walls, complete with all necessary fittings and accessories, installed as per manufacturer’s specifications and standards. Make: Euronics or approved equivalent | NOS | 2 | 3135 | 6270
46 | for handicapped toilets - Fixed Type | NOS | 2 | 4442 | 8884
47 | for Handicapped toilets - foldable type | NOS | 2 | 7125 | 14250
48 | Floor Trap (FT) - cast-iron / SS body, 100 mm dia, with grating SS 304 grating, 100 mm dia, for toilet floor drainage Trap depth 50 mm, removable for cleaning | NOS | 10 | 1188 | 11880
49 | Nahani Trap - cast-iron, 75 mm, with seal | NOS | 6 | 1473 | 8838
50 | Gully Trap (GT) - with screwed cover, for external drainage | NOS | 2 | 3325 | 6650
51 | UPVC SWR Pipe - 110 mm (4") - Soil + Vent stack Astral / Supreme / Prince / Finolex per IS 13592 Type B Includes: elbows / tees / reducers / cleanout / cap fittings Includes: GI brackets / clamps / supports per IS 5572 | RMT | 80 | 595 | 47600
52 | UPVC SWR Pipe - 75 mm (3") - Waste branch / urinal stack Same family (Astral / Supreme / Prince) Inclusive of fittings + supports (Waste branches) | RMT | 60 | 438 | 26280
53 | UPVC SWR Pipe - 50 mm (2") - Floor drain branches / basin / shower waste | RMT | 80 | 333 | 26640
54 | UPVC SWR Pipe - 40 mm (1.5") - Basin trap / lavatory waste | RMT | 60 | 273 | 16380
55 | UPVC SWR Vent Pipe - 75 mm (3") - branch vent | RMT | 40 | 403 | 16120
56 | UPVC SWR Vent Pipe - 50 mm (2") - branch vent | RMT | 30 | 315 | 9450
57 | Vent Cowl - GI / SS, with bird-screen, terrace termination | NOS | 4 | 1295 | 5180
58 | Cleanout (CO) Plug - brass / bronze, threaded, at base of stacks + branches | NOS | 12 | 1250 | 15000
59 | Floor-mounted Inspection Chamber (FRP / SS, sized 200 x 200 / 300 x 300 mm) | NOS | 6 | 6500 | 39000
60 | CPVC Pipe - 32 mm (1¼") - main riser / sub-header Astral / Supreme / Ashirvad CPVC SDR-11 Includes: fittings (elbow / tee / coupling / reducer) Includes: brackets + supports | RMT | 30 | 508 | 15240
61 | CPVC Pipe - 25 mm (1") - sub-branches | RMT | 60 | 385 | 23100
62 | CPVC Pipe - 20 mm (¾") - fixture branches | RMT | 100 | 315 | 31500
63 | CPVC Pipe - 15 mm (½") - fixture connection | RMT | 80 | 228 | 18240
64 | CPVC Solvent Cement + Cleaner + Primer + Tape - installation consumables | LS | 1 | 8500 | 8500
65 | Ball Valve - brass, 32 mm (full bore, lever-operated, isolation at riser) Audco / Zoloto / Sant brass body, full-port, FRC handle | NOS | 2 | 2275 | 4550
66 | Ball Valve - brass, 25 mm (sub-branch isolation) | NOS | 4 | 1575 | 6300
67 | Ball Valve - brass, 20 mm (zone isolation per toilet / cafe) | NOS | 8 | 1015 | 8120
68 | Stop Cock - CP brass, 15 mm (per fixture) | NOS | 30 | 875 | 26250
69 | Water Hammer Arrestor - bellows type, 15 mm dia, brass | NOS | 6 | 1995 | 11970
70 | Pressure Reducing Valve (PRV) - brass, 32 mm, set 4 bar If incoming water pressure > 4 bar (BB tap-off pressure) | NOS | 1 | 5950 | 5950
71 | Air Release Valve - brass, 15 mm, automatic | NOS | 2 | 1155 | 2310
72 | Drain Valve - brass, 15 mm, with hose-tail | NOS | 6 | 665 | 3990
73 | 1450 CFM, 25MM ESP -Toilet Exhaust | NOS | 1 | 29000 | 29000
74 | 1000 CFM, 25MM ESP -Toilet Exhaust | NOS | 1 | 22000 | 22000