## Civil And Interior Works
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Pest Control | Sqm | 371 | 80 | 29680
2 | Type 02 - 150mm Thk AAC Block Masonry | Sqm | 65 | 1750 | 113750
3 | Plastering Works | Sqm | 130 | 490 | 63700
4 | Type 02 - Size of Lintel : 150mm x 150mm | Rmt | 6 | 850 | 5100
5 | Type 03 - Average Thickness of 75-100mm | Sqm | 371 | 750 | 278250
6 | Cinder Filling | Sqm | 4 | 1400 | 5600
7 | Water Proofing (For Floor + Walls 450 mm High) | Sqm | 4 | 1100 | 4400
8 | Type 02 (Size: 150mm - 200mm Dia) | Nos | 2 | 2000 | 4000
9 | 100mm Thk Full Height Gypsum Partition With G I Frame Works From Ffl To True Ceiling | Sqm | 247 | 3000 | 741000
10 | 100mm Thk Baffle Partition With G I Frame Works Above Glazed/ Demountable Partition | Sqm | 41 | 3000 | 123000
11 | Type 01 - Single layers of Gypsum Board Paneling with G.I Framework | Sqm | 50 | 1500 | 75000
12 | Full Height Fire Rated Gypsum Partitions Upto To Structural Ceiling And Above Fire Rated Glass Partition, Doors & Fire Curtains | Sqm | 4 | 5500 | 22000
13 | Type 02 - Cladding of Single Layer 12mm thk Commercial Ply Board | Sqm | 104 | 1550 | 161200
14 | Type 04 - Cladding of Single Layer 6mm thk Commercial Ply Board | Sqm | 60 | 1200 | 72000
15 | Type 01 - Plain White Color | Sqm | 398 | 380 | 151240
16 | Type 02 - Accent Color | Sqm | 165 | 400 | 66000
17 | Paint For Ducts & Other Services In Open Ceiling (Leed Compliant) | Sqm | 149 | 300 | 44700
18 | Oil Based Primer | Sqm | 132 | 280 | 36960
19 | Type 04 - Vitrified Tile Dado Basic Price @ 120/- per Sft | Sqm | 11 | 2400 | 26400
20 | Pop Punning | Sqm | 325 | 360 | 117000
21 | Laminate Cladding With Ply Backing | Sqm | 35 | 2200 | 77000
22 | Reception Backdrop - Metal Fabrication with Metallic paint | Sqm | 24 | 5500 | 132000
23 | Type-04 - 12mm Thk Acoustic Paneling (Plain Finish) - Basic Price @ 180/- per sft | Sqm | 35 | 2500 | 87500
24 | Type-05 - 12mm Thk Acoustic Paneling (CNC Cut 'V' Groove Design/ CNC Cut Design Screen Panels) - Basic Price @ 280/- per sft | Sqm | 32 | 3800 | 121600
25 | Type 02 - 6mm thk (Pearl White/ other Colours) Planilaque Evolution Colored Lacquer Glass cladding on existing ply backing (Non Toughened) - Basic price of (Pearl White/ other Colours) Laquered Glass @ 220/- per sft (Non Toughened) | Sqm | 60 | 3200 | 192000
26 | Laminate Finish Receessed Pen Tray | Rmt | 7 | 2000 | 14000
27 | Type 05 - Basic Price of Wall Paper @ 200/- per Sft | Sqm | 77 | 2450 | 188650
28 | Corner Guards In Alround The Columns | Rmt | 74 | 400 | 29600
29 | Cushion Paneling | Sqm | 7 | 3000 | 21000
30 | L/U/T-Profile -T Profile Golden , | Rmt. | 50 | 400 | 20000
31 | Type 05 - Heritage Tile Flooring Basic Price @ 195/- per Sft (Bharat Flooring & Tiles or Equivalent make) Note: Tile shall be laid as per manufacturers Instructions for Laying. Cost to include polishing of tile after laying: with an Italian polishing machine a week after laying. | Sqm | 58 | 2400 | 139200
32 | Type 02 - Italian Marble Flooring Basic Price @ 800/- per Sft | Sqm | 34 | 14000 | 476000
33 | Type 01 - Antistatic Vinyl Flooring as per selection/ Manufacturer specification - Basic Price @ 150/- per Sft | Sqm | 13 | 1800 | 23400
34 | Foot Mat | Sqm | 6 | 6000 | 36000
35 | Type 01 (Oval Shape) | Sqm | 10 | 7500 | 75000
36 | Type 02 - Plain Gypsum Board Ceiling without Paint & Primer | Sqm | 213 | 1400 | 298200
37 | Gypsum Cove | Rmt | 57 | 450 | 25650
38 | Exposed Ceiling Paint | Rmt | 37 | 380 | 14060
39 | Type 05 - Size : 150-200mm (W) x 400mm to 1000mm (H) | Rmt | 27 | 1800 | 48600
40 | Reception Table Finished In Solid Acrylic Surface Top & Front Facia And Inner Side Finished In Laminate | No. | 1 | 120000 | 120000
41 | Type 01 - 18-20mm thk Prepolished Granite Stone Finish Counter Top with facia (Basic Price of Granite @ 150/- per Sft) | Sqm | 3 | 20000 | 60000
42 | Type 01 - Counter top & Facia to be formed of 18mm thk commercial plywood finished with 1mm thk laminate with edges built upto form overall thickness of 40mm. (Basic Price of Laminate @ 40/- per Sft) | Sqm | 2 | 20000 | 40000
43 | Water Bottle Dispenser Storages | Sqm | 3 | 18000 | 54000
44 | Laminate Finish Over Head Storage | Sqm | 8 | 15000 | 120000
45 | Av Credenza Laminate Finish | Sqm | 3 | 15000 | 45000
46 | Type - 01 (Full Height Storage formed out of Commercial Ply & Finished with Laminate) - 450mm - 500mm (D) | Sqm | 3 | 15000 | 45000
47 | Type - 01 - 450mm (D) | Sqm | 4 | 14000 | 56000
48 | Seating With Cusion | Rmt | 3 | 15500 | 46500
49 | Laminate Portal At Side & Above Breakout Counter | Rmt | 10 | 3000 | 30000
50 | Steps For Raised Floor (Wooden Frame Work With Ply Cladding Finished In Laminate) | Sqm | 1 | 6000 | 6000
51 | Meeting Room Table - Marble Top | Nos | 1 | 80000 | 80000
52 | Propreitary Aluminum Transition Strip | Rmt | 22 | 300 | 6600
53 | Trap Door | Sqm | 5 | 6000 | 30000
54 | Modular Type Trap Door - 450x450 | Nos | 4 | 4200 | 16800
55 | Modular Type Trap Door - 600x600 | Nos | 4 | 5800 | 23200
56 | Waste Bins Units At Pantry/Breakout | Nos | 1 | 8500 | 8500
57 | Waste Bins Units At Repro | Nos | 1 | 2000 | 2000
58 | Type 01 (Small Size) - (Model No. AFBR 3FP of Euronics or equivalent approved make) Size :10" dia x 14" ht (considered 1 nos. between 2 workstation) | Nos | 30 | 950 | 28500
59 | Type 02 (Big Size) - Model No. AFBP 3FP, Perforated Pedal Bin with Inner Removable Container of Euronics or equivalent approved make Size :11 Ltr - 10"dia X 15" ht | Nos | 4 | 1050 | 4200
60 | Fire Sealent | Sqm | 2 | 2000 | 4000
61 | Ply Support For The Cassette Units | Nos | 4 | 2000 | 8000
62 | Ms/ Wooden/ Ply Support For The AC Ducts | Nos | 4 | 1500 | 6000
63 | Ply Backing Support For The Light Fixtures & Speakers | Nos | 4 | 550 | 2200
64 | Wooden Frame For Floor Junction Boxes | Nos | 4 | 1500 | 6000
65 | Type 02 - Size : 250mm to 300mm Wide postform laminated window sill as per detail drawing | Rmt | 27 | 1750 | 47250
66 | Security Guard | Month | 2 | 40000 | 80000
67 | House Keeping & Deep Cleaning For Complete Project Works | Sqm | 343 | 200 | 68600
68 | Site Office Items On Rental Basis | LS | 1 | 75000 | 75000

## Raised Flooring Works
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 300mm High Raised Access Floor with Antistatic Laminate Finish Panel | Sqm | 7 | 4900 | 34300

## Graphics, Frost Film & Internal
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Type 03 - Wall Décor Ultra - IJ1220C Micro Comply Base Material With 8157M Over Laminate (1 Years Warranty) | Sqm | 55 | 1800 | 99000
2 | Type 01 - Optical Clear View Décor Effect Film 8150 with WDT02 (3 Years Interior Warranty) | Sqm | 47 | 1750 | 82250
3 | Logo | Nos | 1 | 25000 | 25000
4 | Pull Push Signages | Nos | 16 | 550 | 8800
5 | Fire Exit Double Sided Signage | Nos | 2 | 1500 | 3000
6 | Fire Exit Single Sided Signage | Nos | 2 | 1200 | 2400
7 | Fire Extinguisher Signage | Nos | 2 | 550 | 1100
8 | Fire Evacuation Map | Nos | 2 | 7500 | 15000
9 | Pictograms (Ss Door Signage) For Toilets & Janitor | Nos | 2 | 750 | 1500
10 | Room Signages | Nos | 16 | 750 | 12000
11 | Reception Legal Signage | Nos | 1 | 7500 | 7500
12 | Workstation Signage | Nos | 35 | 750 | 26250
13 | No Smoking Signages | Nos | 2 | 2000 | 4000
14 | Floor Level Indicator Signages | Nos | 1 | 1800 | 1800

## Racks Compactors & Lockers
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Type 02 - Size of Rack: 900mm (W) x 450mm (D) x 2100mm (H) | Nos | 5 | 6500 | 32500

## Toilet Finishes Works
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Type 01 - 150mm thk ACC Block Masonry Wall | Sqm | 51 | 1750 | 89250
2 | Plastering Works | Sqm | 102 | 490 | 49980
3 | Sunken/ Raised Filling | Sqm | 11 | 1400 | 15400
4 | Water Proofing (For Floor + Walls 450 mm High) | Sqm | 11 | 1100 | 12100
5 | CORE CUTTING | Nos | 2 | 2000 | 4000
6 | Type 01 - Szie of Lintel : 150mm x 150mm | Rmt | 4 | 850 | 3400
7 | Type 01 - Vitrified Tile Flooring Basic Price @ 90/- per Sft | Sqm | 11 | 2100 | 23100
8 | Granite Ledge Wall | Rmt | 4 | 2500 | 10000
9 | Type 02 - Vitrified Tile Flooring Basic Price @ 90/- per Sft | Sqm | 37 | 2100 | 77700
10 | Mirror Paneling (6mm Thk) With Ply Backing | Sqm | 4 | 5650 | 22600
11 | 600mm x 600mm x 0.5mm Thk Modular Metal Grid Ceiling Works - Exposed 15mm 'T' Grid System with Galvanised Plain Tile | Sqm | 11 | 1950 | 21450
12 | Washbasin Counter Granite Top | Sqm | 2 | 5500 | 11000
13 | Granite Door Jamb | Rmt | 13 | 1450 | 18850
14 | Granite Umara Patti | Rmt | 3 | 1400 | 4200
15 | Single Leaf Laminate Finish Flush Door with Granite Door Frame/ Jamb & MS Poder coated Louvers - SIZE : 900mm x 2400mm (D__) | Nos | 2 | 32000 | 64000

## BOQ-SF
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Type 09 (Linear Workstations) - Size: 1200mm L x 600mm D x 750mm ht | Nos | 27 | 22500 | 607500
2 | Type 09 ('L' Shape Workstations) - Size: 1500mm L x 1200mm W x 600mm D x 750mm ht | Nos | 8 | 32000 | 256000
3 | • Rectangular Meeting Tables ¦ 4 Pax ¦ Overall size 1500mmx1200mm • Finish: Laminate finish • Flip top box: 1 | Nos | 1 | 25500 | 25500
4 | Type 01 - 3 Drawer Pedetal Unit (2+1) | Nos | 39 | 7500 | 292500
5 | Type 01 (Cabin Table) - Main Desk Size: 1500mm x 750mm | Nos | 4 | 49000 | 196000
6 | Type 01 (Cubical Desk) - Overall Size: 2400mm x 2000mm Main Table - 2100mm x 750mm (with Pedestal) Side Credenza - 1200mm x 450mm | Nos | 4 | 54000 | 216000
7 | Type 01 - Full Height Storage Cabinet - D600mm X H2400mm | Sq.M. | 11 | 27500 | 302500
8 | Type 01 - Planter stoarge - H1050mm X D450mm | Nos | 5 | 29900 | 149500

## BOQ-Chair
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Medium Back Chairs | No. | 48 | 19500 | 936000
2 | High Back Chairs | No. | 12 | 38000 | 456000

## BOQ-Carpet
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Carpet Type 1 Make: As Per Make List Density:Min 16Oz/Yd2 - 18 Oz/Yd2 | Sq.M. | 245 | 1820 | 445900
2 | Carpet Type 2 Make: As Per Make List Density:Min 16Oz/Yd2 - 18 Oz/Yd2 | Sq.M. | 15 | 2070 | 31050
3 | Carpet - Installation (Type-01) | Sq.M. | 230 | 130 | 29900
4 | Carpet - Installation (Type-02) | Sq.M. | 10 | 130 | 1300

## PHE - TOILET
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply, Installing, testing and commissioning of White colour wall mounted European water closet with concealed flush tank with necessary pan connecter, bend,checknut, solid seat cover with polythene buffer and flap etc.,(The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning ) complete. The flow rate of fixture shall be as per IGBC requirement. | Nos | 2 | 16500 | 33000
2 | Supply, Installing, testing and commissioning of under counter wash basin, 15mm dia Pillar cock with waste coupling, 32mm dia CP bottle trap with extension pipe, supporting bracket with necessary steel to support basin 1 No.15mm CP angle valve with 450mm long CP connection pipe and CP wall flanges all of approved make etc.,(The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning ) complete. The flow rate of fixture shall be as per IGBC requirement. | Nos | 2 | 15500 | 31000
3 | Supply, Installing, testing and commissioning of 15mm CP health faucet of approved make with necessary CP flexible hose 1000mm long nozzle wall flange, CP angle cock etc., (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning ). The flow rate of fixture shall be as per IGBC requirement. | Nos | 2 | 3200 | 6400
4 | Supply, Installing, testing and commissioning of Stainless sink with single bowl manufactured from 1mm thick stainless steel, 18G high grade indestructible chrome nickel steel with top quality polish,1no.40mmdia CP waste coupling, Sink cock with wall flange with aerator etc., complete. For Kitchen/Cafe/Wet Pantry. | Nos | 2 | 12000 | 24000
5 | Supply, Installing, testing and commissioning of 15 mm dia CP Angle cocks (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning)complete. | Nos | 6 | 3000 | 18000
6 | Supply, Installing, testing and commissioning of Horizontal / Vertical type electrical water heater of up to 15 Liters capacity including support, 2 Nos CP angle valve, connection hose, support etc. Complete | Nos | 1 | 18500 | 18500
7 | Supply and fixing of 1000 ml Liquid soap dispenser with SS screws on the wall. | Nos | 4 | 1700 | 6800
8 | Supply and fixing of Stainless steel body paper towel dispenser with SS screws on the wall | Nos | 3 | 2500 | 7500
9 | Supply and fixing of Hand Dryer ( Heavy Traffic ) with SS screws on the wall. | Nos | 3 | 11000 | 33000
10 | Supplying, Fixing CP toilet paper holder fixed with SS screws complete. | Nos | 2 | 950 | 1900
11 | Supplying, Fixing CP twin coat hook fixed with SS screws on to the toilet door. | Nos | 2 | 520 | 1040
12 | 75mm dia (low noise pipe) | Rmt | 12 | 700 | 8400
13 | 110mm dia (low noise pipe) | Rmt | 24 | 850 | 20400
14 | 40mm dia (low noise pipe) | Rmt | 8 | 570 | 4560
15 | 50mm dia (low noise pipe) | Rmt | 6 | 630 | 3780
16 | Supply and fixing of PVC self cleasing, deep seal type 110 mm dia Multi Floor trap and 75mm outlet with necessary cement concrete, water proofing the internal surfaces of chamber etc.,or laid under floor / under ceiling / on walls with suitable clamps including making bores in masonry etc., and rendering the bores in cement mortar after laying the pipes and specials curing etc., complete as per specifications. depth of trap shall not be less than 125mm.(The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning) complete | Nos | 4 | 4000 | 16000
17 | Supply and fixing of cockroach trap of size 153mm x 153mm, complete as per specifications. (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning) complete | Nos | 4 | 1400 | 5600
18 | Supplying and fixing MS angle brackets, hangers, supports as required for supporting pipes with suitable GI U- clamps, bolts, nuts and washers etc. The clamps shall be painted with two coats of enamel (approved) paint over a coat of primer etc., complete. | Kgs. | 3 | 140 | 420
19 | Supply, fixing and testing of Garbodrain G-1000 (Food waste crusher), including all fittings, should be anti-jam impellers made of SS 304 for efficient grinding & corrosion free, run with AC power supply with calling bell switch for dry run protection. (for pantry, pot wash area) | Nos | 2 | 50000 | 100000
20 | 150x60mm | Rmt | 16 | 400 | 6400
21 | SFA Sanigreease traps-Grease separator below counter (grease trap Undersink, Standard, or equivalent,.), For Pantry area,. | Nos | 1 | 30000 | 30000
22 | 20mm Dia | Rmt | 26 | 400 | 10400
23 | 25mm Dia | Rmt | 8 | 450 | 3600
24 | 32mm Dia | Rmt | 12 | 500 | 6000
25 | 20mm Dia | Nos | 2 | 400 | 800
26 | 25mm Dia | Nos | 3 | 550 | 1650
27 | 32mm Dia | Nos | 2 | 700 | 1400
28 | 32mm Dia | Nos | 2 | 25000 | 50000

## FA
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply Installation Testing & Commissioning of Analogue Addressable Intelligent networkable 01-Loop Fire alarm control panel, provision to make with a minimum capacity of 125 devices + 125 modules per loop, with battery back up for 24 Hrs during normal operation and 15 minutes alarm operation, with minimum 640 Character LCD display, necessary interface card to connect a repeater panel and all hardware & software as per specification. Battery bank should be with enclosure. Panel shall be seamleasly communicate with other panels, Rate shall inclusive of loop cards,POWER SUPPLY UNITS,BATTERY,CABINET...ETC. Each loop shall be loaded with 80% devices of manufacturer specified capacity. The control panel shall be capable of expansion up to 04 SLC modules. *** Panel Loop card qty as per OEM configuration from the Approved makes list The panel shall be UL listed & FM approved, panel shall be 10th Edition / latest edition as per OEM. The panel shall preferably be programmable without any authorisation dongle and laptop as well as software. In case the dongle/software is required, the same shall be handed over to client and shall also be available with minimum two independent service providers. | Nos | 1 | 110000 | 110000
2 | Supply Installation Testing & Commissioning of multi sensor detector (photo+heat) with base,powder coated back box and other accessories as required and Detectors shall be UL listed 268 7th edition and FM Approved - True Ceiling / Above False Ceiling Locations | Nos | 6 | 4900 | 29400
3 | Supply Installation Testing & Commissioning of Analog Addressable Smoke Detector with programmable for timed automatic sensitivity selection with Standard base, MS powder coated backbox and other accessories as required and Detectors shall be UL listed 268 7th edition and FM Approved. (ABOVE FALSE CEILING /TRUE CEILING) | Nos | 24 | 4200 | 100800
4 | Supply Installation Testing & Commissioning of Analog Addressable Smoke Detector with programmable for timed automatic sensitivity selection with Standard base and other accessories as required and Detectors shall be UL listed 268 7th edition and FM Approved-(BELOW FALSE CEILING) | Nos | 24 | 4200 | 100800
5 | Supply Installation Testing & Commissioning of Heat detector (Fixed with base, MS powder coated backbox and other accessories as required and Detectors shall be UL listed 268 7th edition and FM Approved. (BELOW FALSE CEILING)@ Kitchen /Pantry Areas. | Nos | 1 | 3600 | 3600
6 | Supply Installation Testing & Commissioning of Response indicator with LED display for all detectors located above false ceiling. | Nos | 27 | 1250 | 33750
7 | Supply Installation Testing & Commissioning of Analogue Addressable Fault isolator module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected. (FIM's are used for every 20 detectors/devices). MS powder coated backbox and other accessories as required | Nos | 2.75 | 3200 | 8800
8 | Supply Installation Testing & Commissioning of Analogue Addressable Monitor module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact. MS powder coated backbox and other accessories as required BB INTEGRATION#1 PA #1 Acs#0 FLOW SWITCH#1 WLD#2 RRS##0 SPARE#1 | Nos | 6 | 3500 | 21000
9 | Supply Installation Testing & Commissioning of Analogue Addressable Control module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact.MS powder coated backbox and other accessories as required ACS TRIP#0 HOOTER#2 BB INTEGRATION#1 SPARE#1 | Nos | 4 | 7000 | 28000
10 | SITC Analogue Addressable Control relay module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact. MS powder coated backbox and other accessories as required Electrical Panel #1 AHU,CSU & FD #2 ACS Panel Tripping#4 BB INTEGRATION#0 Spare#1 | Nos | 8 | 3500 | 28000
11 | Supply Installation Testing & Commissioning of Addressable Electronic Hooter cum Strobe ceiling mounted. The hooters shall be made of ABS plastic, and have a DB level of 65dbA and a multi tone facility. Addressable Control Module shall be fitted in a junction box . Rate shall inclusive of MS powder coated backbox and other accessories as required | Nos | 2 | 5500 | 11000
12 | Supply Installation Testing & Commissioning of Addressable Manual call point with protective cover having an integrally mounted addressable module that monitors and reports contact status. (DUAL ACTION TYPE). Rate shall inclusive of metal backbox including necessary civil works | Nos | 2 | 2450 | 4900
13 | FAS CABLE- 2C x 1.5 mm2, Stranded Annealed Bare Copper conductor,CU Cable 1100 v, Type A , ST1 PVC insulated, PVC Inner sheathed,GI wire Armoured with FRLS outer sheath (1.24 thick) as per IS 1554-1 Cable Marking should include ISI marking& CM/L number. CU Cable with GI saddle spacers every 0.3 mtr with Single compression Cable Glands (metal) ,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Rmt | 1000 | 110 | 110000
14 | 25 mm dia. | Rmt | 20 | 40 | 800
15 | Supply and laying of MS Powder coated Trunking 100 x 50 mm x 1.6mm with cover & fixing suppports etc as required (Cable dressing for Fire & PA panel ) | Rmt | 2 | 950 | 1900
16 | Supply Installation Testing & Commissioning of PSU for hooters & Repeater Panel (inclusive of Battery ckt & battery), CE Approved | Set | 1 | 1500 | 1500

## PA
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | SITC of 6W RMS False Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with mounting clamps as per specifications or equivalent as per OEM. - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range(-10 dB) : 150 Hz to 15KHz - SPL at rated power (1Khz at 1 m) 108 dB - Opening Angle 1 KHz / 4 KHz (-6 dB): 180/45 | Nos | 21 | 1250 | 26250
2 | SITC of 6W RMS True Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with powder coated back box, supports as per specifications or equivalent as per OEM. - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range(-10 dB) : 150 Hz to 15KHz - SPL at rated power (1Khz at 1 m) 108 dB - Opening Angle 1 KHz / 4 KHz (-6 dB): 180/45 | Nos | 3 | 1550 | 4650
3 | SITC of 6W Wall Mounted / Cabinet Speakers with line matching transformers specified as per above said specifications. | Nos | 1 | 1550 | 1550
4 | Supply,installation ,testing & Commissioning of 8 / 12 zone Voice Alarm Main Controller having features like announcement to 8 zone, input port of emergency microphone on the front panel, music to selected zones can be played, built in 1 GB memory for audio files,volume adjustment with digital volume control. as per technical specification etc. as required. | Nos | 1 | 150000 | 150000
5 | 240W | Nos | 1 | 60000 | 60000
6 | Supply,installation ,testing & Commissioning of voice Alarm Call Station having gooseneck condenser Microphone with 16 zone Selection Keys and an All-Call-Key, PTT Switch, selectable gain, speech filter and limiter for improved intelligibility,LED indication for zone selection complete as required, | Nos | 1 | 42000 | 42000
7 | PAS CABLE- 2C x 1.5 mm2, Stranded Annealed Bare Copper conductor,CU Cable 1100 v, Type A , ST1 PVC insulated, PVC Inner sheathed,GI wire Armoured with FRLS outer sheath (1.24 thick) as per IS 1554-1 Cable Marking should include ISI marking& CM/L number. CU Cable with GI saddle spacers every 0.3 mtr with Single compression Cable Glands (metal) ,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Mtrs | 250 | 110 | 27500
8 | SITC of Volume controller for one speaker (Rational qty / item) | Nos | 1 | 1200 | 1200
9 | SITC OF Suitable size rack as per following specification, Conforms to DIN 41494 Or Equivalent EIA/ISO/EN/CEA Standard Finish - Powder coated finish with Seven tank pretreatment process meeting ASTM standard. shall be of mild steel with suitable anticorrosion protective coating Color - Black/off white/grey Fan module on top of the rack Welded frame with vented top cover with fan , perforated Metal Door with lock & Key and Back vented / Perforated metal door with lock & key and partially vented side panels, free standing on floor with 4 No. casters wheels with 2 no with brakes & 2 No. without brakes, cable oraginesers, Levelers with required 16A/5A power strips including accessories.The racks shall have lockable steel doors having proper ventilation slots for heat dissipation. Cable entry parts should be provided at the bottom. Number of racks shall be as per the design requirement. vendor to consider required number of racks as per their requirement 80% Loading of the rack to be considered. | No | 1 | 15000 | 15000

## FPS
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 25mm nominal dia | Rmt | 120 | 480 | 57600
2 | 32mm nominal dia | Rmt | 30 | 580 | 17400
3 | 40mm nominal dia | Rmt | 30 | 660 | 19800
4 | 50mm nominal dia | Rmt | 18 | 800 | 14400
5 | 65mm nominal dia- | Rmt | 12 | 1030 | 12360
6 | 80mm nominal dia | Rmt | 18 | 1200 | 21600
7 | 100mm nominal dia | Rmt | 12 | 1440 | 17280
8 | b) Pendent - 68deg C @ BFC | Nos | 35 | 900 | 31500
9 | c) Upright - 68deg C | Nos | 35 | 960 | 33600
10 | Supplying, installing, testing and commissioning of 25mm dia Sight glass unit for sprinkler drain, drain valves, ball valves, check valves, Union etc. complete.Set shall be UL Listed | Nos | 1 | 7500 | 7500
11 | GLYCERINE FILLED Dial type pressure guage for (0-16 Kg/cm2) with necessary nipple & other fittings, mounting arrangements and with a 15 mm ball valve | Nos | 1 | 960 | 960
12 | Supply, Installation, Testing & Commissioning of 25mm Ball valve with sight glass for Sprinkler test line | Nos | 1 | 1550 | 1550
13 | Supply, Installation, Testing & Commissioning of 50mm Ball valve for Sprinkler drain line | Nos | 1 | 2550 | 2550
14 | 100 NB | Nos | 1 | 4500 | 4500
15 | 100mm dia | Nos | 1 | 8500 | 8500
16 | The Rosette shall be fabricated by M.S. plate of 2mm thick and the finish shall be powder coated and color shall be as approved by architects / clients. | Nos | 35 | 450 | 15750
17 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed & FM Approved, 16 bar pressure rating and 1500 mm long 25 mm dia with union / reducer collar, clamps etc. as required. (BRAIDED) - To be connected to existing sprinkler network with required fittings/accessories | Nos | 35 | 1200 | 42000

## FE
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | CO2 stored pressure type Fire Extinguisher ISI marked confirming to IS:15683 latest. Capacity 4.5 Kg. Complete with delivery hose horn, squeeze grip release valve, locking arrangement,operating temperature -30°C to +55°C, supplied with body bearing IS 7285 mark and approved by CCoE tested at 250 kgf/cm2., fitted with ISI marked & CCoE approved valve as per IS 3224. CO2 Gas as per IS: 15222. externally painted with PO Red Shade No. 538 of IS 5, operation manual and tripod floor stand or Wall Mount Bracket including accessories as required as per site condition | Nos | 1 | 6500 | 6500
2 | Powder type Fire Extinguisher (Stored Pressure type) (Powder pressurized with dry nitrogen gas at 15 bar.) capacity: 6kg duly ISI marked conforming to IS: 15683:2006/latest, with IS 14609 ISI marked ABC powder complete with squeeze grip release valve, discharge pipe, locking arrangement, pressure gauge, operation manual,Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, and floor stand or Wall Mount Bracket including accessories as required as per site condition | Nos | 4 | 4500 | 18000
3 | FE36 Automatic ceiling Mounted Clean agent Extinguisher - 5 Kg with Ceiling mount accessories including nozzle(57 deg), pressure guage. ISI approved. SERVER, BATTERY & UPS ROOMS | Nos | 3 | 28000 | 84000

## RODENT
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply, Installation, Testing and Commissioning of Networkable Master Controller Rodent Repellant Panel with a capability to connect atleast 1-12 transducers per controller with RS485 modbus integration.The operating frequency shall be > 20kHz and < 75kHz. The front fascia shall have a LCD display and on board controls to change, view and operate the menu (12 TRANSDUCER PER CONSOLE) | Nos | 1 | 32000 | 32000
2 | SITC of Transducer capable of Emitting Ultrasonic sound of frequencies 20 Khz and higher, with blinking LED Indication & shall capable to covering area of Mini.150 Sq ft in floor & ceiling void and 300Sqft in Room void. Rate shall inclusive of 1.6mm thick suitable size metal back box | Nos | 6 | 6000 | 36000
3 | SITC of 1 pair flexible 14/40 SWG Specially coated wire, PVC sheathed Cable | Mtrs | 100 | 90 | 9000
4 | Supply and surface laying of 25mm dia 2mm thick PVC FRLS Conduit with GI Saddels and spacers at every 0.3 meter | Mtrs | 100 | 40 | 4000
5 | Supply and laying of GI enclosed raceway 50 x 50 mm x 1.6mm with cover & fixing suppports etc as required (Cable dressing ) | Mtrs | 2 | 400 | 800

## WLD
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply Installation, Testing & Commissioning of Water leak cable sensor as per tender specification. Water leak sensing cable shall be twisted, mechanically strong, resistant to corrosion and abrasion. The cable shall be constructed with two sensing wires, an alarm signalling wire and a continuity wire. | Nos | 30 | 750 | 22500
2 | Supply, Installation of Leak detection system 4 zone control Digital Panel with Display, Power supply & all required accessories including module . The panel should have the capability /features to integrates with BMS. | Nos | 2 | 75000 | 150000
3 | Sounder - 75 db @ 1 mtr (HOOTER OUTSIDE ROOM) | Mtrs | 2 | 2000 | 4000
4 | Control Cables : 2 CORE x 1.5 mm2, Stranded ABC conductor,Type A ST 1 PVC insulated,Armoured FRLS Cable 650 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Mtrs | 10 | 90 | 900

## ACS
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Supply, Installation, Testing and Commssioining of RS485 based Single Door(2 Readers) Access Controller , power supply unit, TCP IP connectivity with tamper detection provision as per the tender specifications. Cost shall including enclosure for controller and power supply unit for controller (power supply unit shall inclusive of battery backup with exhaust fan). | Nos | 4 | 40000 | 160000
2 | Supply, installation, testing & commissioning of Multi smart Card readers along with 5mm mullion spacer plate / wall switch adapter plate with 2.5mm thick SS front plate as per specification Supporting for MIFARE Classic, MIFARE ultralight, MIFARE DESFire, HID Prox CE Approval suitable for mounting on metal surface/metal frames or wooden frames wall or as required based on site conditions including all accessories.-All ACS Doors & Turnstile | Nos | 8 | 15500 | 124000
3 | Supply, installation, testing and commissioning of Proximity Access Cards with Lanyard to hold the cards as per specification. | Nos | 100 | 90 | 9000
4 | Supply, Installation, Testing and Commssioining of Electromagnetic Lock with required mounting brackets for single door as per the tender specifications | Nos | 4 | 6000 | 24000
5 | Supply, Installation, Testing and Commssioining of surface / flush mounted (as required at site) Magnetic Contact (Door position sensor) for access controlled doors as per the tender specifications | Nos | 4 | 1200 | 4800
6 | Supply, Installation, Testing and Commssioining of Panic Button/switch with accessories (Reception Table) | Nos | 1 | 1200 | 1200
7 | Supply,Installation, Testing and Commssioining of the Security Management Server software and also proivde Integrated Access Management 1 Master Software for Access Control & Time & attendance software with alarm monitoring as per the tender specifications-I Amp model | Set | 1 | 200000 | 200000
8 | Supply, Installation, Testing and Commssioining of security Management Software PC Server Station with minimum Intel i5 2.6 Ghz processor, 4 GB RAM, NVIDIA Graphics card with 1GB, 500 GB HDD, 24" Color flat panel LED Monitor,500TVL, 1080P HD Resolution, 100/1000Mbps network card with original Microsoft Windows 8 Operating System or higher, antivirus softwares,MS softwares. These PC (1#) will be loaded with Security Management Server software Master Software, Access Control & Alarm Monitoring. | Set | 1 | 75000 | 75000
9 | Supply and laying of 4 core 1.0 Sq mm Un Armoured Shielded FRLS, Multistanded Copper Conductor, PVC sheathed Cable for connecting controller to Lock & door position sensors, Buzzer,BGU,Pushbutton as per the tender specifications. | Mts | 150 | 80 | 12000
10 | Supply and laying of 8 core x 1 Sq mm Un Armoured Shielded FRLS, Multistanded Copper Conductor, PVC sheathed Cable for connecting controller to readers as per the tender specifications. | Mts | 150 | 120 | 18000
11 | Supply and laying of MS Powder coated Trunking 300 x 50 mm x 2mm with cover & fixing suppports etc as required | Mts | 10 | 750 | 7500
12 | Supply, Installation, Testing and Commissioning of Buzzer for access controlled doors as specified in the Tender Specifications | Nos | 4 | 750 | 3000
13 | Supply installation, testing, commissioning of EDR (EMERGENCY BREAK GLASS ) - double pole | Nos | 4 | 1200 | 4800
14 | Supply and laying of CAT6 cable including 2mm thick PVC FRLS conduit (cost shall inclusive of accessories) | Mts | 50 | 90 | 4500
15 | Supply and laying of 1" - 2 mm thick FRLS - PVC Conduits,JB's in wall, columns, ceiling etc., including associated civil works. - For ACS cabling from controller to Readers,BGU,EM Lock …etc. Conduit colour shall be in BLUE COLOR | Mts | 50 | 40 | 2000

## CCTV
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | IP Dome camera 2 MP HD 1080P with 1/3" CCD/CMOS, Progressive/De-interlace, Very High Definition resolution (1920x1080), Dual streaming, 25 FPS, min one H.264 stream & one H.264/MPEG 4 stream compression support, 2.7-12mm lens, 0.1 lux, Tamper detection with built in WDR & automatic back light compensation circuitry with camera manufacturer's power supply unit and with built in WEB Browzer and required wall / ceiling mounted accessories as specified in the Tender Specifications . The camera shall be capable of operating on both POE and an UPS power source and shall switch seamlessly between the sources. Camera shall be along with Suitable adaptor with 3 meter cable. The camera shall be equipped with in built 32GB memory card which shall be used for recording during periods of server/ network failure. Camera shall be along with camera mounting pole/accessories | Nos | 7 | 7000 | 49000
2 | NETWORK VIDEO RECORDER Supply, installation, testing and Commissioning of 8-channel Network video recorder, with required storage capacity to accomadate 30 days storage at 15 FPS and at 4 CIF resolution for above said quantity cameras, complete with all accessories as required.Required HDD to be considered in the NVR, quoted price is inclusive of all required hardwares,softwares and associated accessories. If vendor requirement is more than what is specified here, the vendor shall quote the configuration that meets their requirement | Nos | 1 | 20000 | 20000
3 | Supply, Installation, Testing and Commssioining of min 40" LED TV with 50" diagonal screen size, Contrast ratio min. 6000:1, Native Resolution : 1080P FULL HD Aspect ration- 16:9, color system - PAL/NTSC, Data signals - VGA, SVGA, XGA, S-Video input, Detachable speakers, wall mount kit with PC Connectivity for Multi screen video display and with anti reflectiver screen coating- DISPLAY MONITORS | Nos | 1 | 30000 | 30000
4 | Supply, installation, testing & commissioning of Client Workstation 64BIT to handle up to 100 cameras (at Low resolution) per monitor with multi monitor support. In order to have a better performance, the following configuration should be considered as minimum which should be sufficient to view in real time up to 24 cameras on HD Resolution. Processor – (1) Intel® Core™ i7-9700 9th Generation Processor (Up to 8 Cores, 8 Threads,4.70GHz) Memory – Minimum 16 GB Hard disks – 256GB M.2 SSD OS - Windows 10 Pro , 64bit Network Card – 1Gbit/s network card GPU : NVIDIA Quadro P2200 HDD : 1TB 3.5" Video Surveillance Grade SATA Drive | Nos | 1 | 150000 | 150000
5 | 8 port 10/100/1000 layer 2 switches with IP multicast snooping and data-driven IGMP support and with minimum two 1000baseT RJ45 uplink ports and twp 1000 baseT Fiber uplink ports and enclosure/rack for switch with mounting supports and all accessories. | Nos | 1 | 28000 | 28000
6 | Supply, installation, testing & commissioning of Supply & Laying of Flexible LSZH Cat-6 cable laid in Conduits / cable Trays. Shall be complete with IO Module Boxes at the Camera End, Patch Cords, GI Gang Boxes, Termination lugs, Labelling and tagging, ferruling etc (this item inclusive of necessary patch cords,I/O's & terminations for connecting camera with network switch) | Mts | 600 | 50 | 30000
7 | Supply and laying of 1" - 2 mm thick FRLS - PVC Conduits,JB's in wall, columns, ceiling etc., including associated civil works. | Mts | 300 | 40 | 12000
8 | Rack and other Accessories as required for CCTV systems (rack shall be powder coated type, enclosed with door opening on front side, ventilation provision & standard dimensions to meet the design requirements) | Set | 1 | 15000 | 15000

## ELECTRICAL
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | MAIN LT PANEL | Nos | 1 | 250000 | 250000
2 | 40A 4P - Outdoor | No. | 2 | 7500 | 15000
3 | 20A DP - Outdoor | No. | 2 | 6500 | 13000
4 | 40A 4P - Outdoor | No. | 4 | 8000 | 32000
5 | Outgoing - 2nos of 63A 4P MCB, 2nos of 32A DP MCB. All D curve MCB's | No. | 1 | 75000 | 75000
6 | 3.5 Core X 50 Sqmm | Mts | 150 | 450 | 67500
7 | End terminations | Nos. | 4 | 850 | 3400
8 | 4 Core X 16 Sqmm | Mts | 240 | 350 | 84000
9 | End terminations | Nos. | 4 | 700 | 2800
10 | 4 Core X 10 Sqmm | Mts | 90 | 280 | 25200
11 | End terminations | Nos. | 8 | 550 | 4400
12 | 1 Core x 16 Sq. mm | Mts | 60 | 120 | 7200
13 | End terminations | Nos. | 8 | 300 | 2400
14 | 1 Core x 6 Sq. mm | Mts | 90 | 90 | 8100
15 | End terminations | Nos. | 12 | 300 | 3600
16 | 3 Core x 10 Sq. mm | Mts | 40 | 220 | 8800
17 | End terminations | Nos. | 4 | 450 | 1800
18 | 3 Core x 4 Sq. mm | Mts | 120 | 150 | 18000
19 | End terminations | Nos. | 16 | 450 | 7200
20 | 4 Core x 10 Sq. mm | Mts | 100 | 250 | 25000
21 | End terminations | Nos. | 4 | 450 | 1800
22 | 4 Core x 6 Sq. mm | Mts | 40 | 180 | 7200
23 | End terminations | Nos. | 4 | 450 | 1800
24 | Outgoing : 24 Nos. 16A SP MCB of 'C' curve | No. | 1 | 75000 | 75000
25 | Outgoing :4 Nos.16A SP MCB of 'D' curve | No. | 1 | 15500 | 15500
26 | Outgoing : 36 Nos. 10A, 10KA, SP MCB of 'D' curve | No. | 1 | 85000 | 85000
27 | Outgoing : 24 Nos. 16A SP MCB of 'C' curve | No. | 1 | 75000 | 75000
28 | Outgoing : 4 Nos.16/20A SP MCB of 'D' curve | No. | 2 | 15500 | 31000
29 | Supply & Installation of 3Rx2.5Sq.mm MSCC wires in 20mm dia PVC conduit as lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / sensor / light point and looping between the switches & sensor ( further onwards, it shall be deemed to be included in point wiring). | Mts. | 300 | 150 | 45000
30 | Supply & Installation of 3Rx1.5Sq.mm MSCC wires in 20mm dia PVC conduit as emergency lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / sensor / light point and looping between the switches & sensor ( further onwards, it shall be deemed to be included in point wiring). | Mts. | 75 | 120 | 9000
31 | Supply & Installation of 3Rx1.5Sq.mm multistrand copper conductor wires in 20mm dia PVC conduit | Mts. | 60 | 120 | 7200
32 | Supply & Installation of 3C x 2.5 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white colour for UPS circuit and black colour for raw power circuit. | Mts. | 800 | 150 | 120000
33 | Supply & Installation of 3C x 4 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white colour for UPS circuit and black colour for raw power circuit. | Mts. | 30 | 180 | 5400
34 | 1x6A socket controlled by 6A switch | Nos. | 20 | 550 | 11000
35 | 2x6/16A socket controlled by 16A switch | Nos. | 5 | 850 | 4250
36 | 2x6A socket controlled by 16A switch | Nos. | 15 | 750 | 11250
37 | 3x6/16A socket controlled by 16A switch | Nos. | 40 | 1050 | 42000
38 | 1x6/16A socket controlled by 16A switch | Nos. | 25 | 650 | 16250
39 | 1x16A socket controlled by 16A switch | Nos. | 2 | 650 | 1300
40 | 6module MS/GI back box for electrical outlets as per site requirement including necessary civil works | Nos. | 5 | 200 | 1000
41 | 3module MS/GI back box for electrical outlets as per site requirement including necessary civil works | Nos. | 5 | 100 | 500
42 | 2module MS/GI back box for electrical outlets as per site requirement including necessary civil works-KEYPAD -LMS | Nos. | 10 | 80 | 800
43 | SITC of MS/GI back box for data outlets as per site requirement including necessary civil works | Nos. | 10 | 70 | 700
44 | 1No. 32A 3 pin 1phase Industrial type socket controlled by 32A MCB with plug top enclosed in sheet metal box with able to mount on wall / raceway with necessary accessories complete as required | Nos. | 2 | 5500 | 11000
45 | I. Primary light point means wiring from first switch control to the first light out let. | Nos. | 18 | 1250 | 22500
46 | I. Secondary light point means extention of light out let only from existing. Primary point to be controlled by the existing switch of Primary point only. | Nos. | 20 | 750 | 15000
47 | I. Secondary light point means extension of light outlet from existing primary point with ceiling rose & complete accessories. Same to be controlled by the existing MCB in DB | Nos. | 85 | 850 | 72250
48 | Recess mounted Occupancy sensor. Supply & installation of IP 20 Class Occu Switch Ceiling Mount Occupancy Detector with detection range of 6m dia recessed and controls LED load of 6A with inbuilt photocell & rotary knobs on the front cover of the sensor to set the lux level & time delay from 30 Sec to 30 Mins and an inbuilt retractable shield to reduce the sensor range, The Occuswitch Sensor shall not consume more than 1.2 Watts of power and complies to IEC (EN) 60669-2-1, IEC (EN) 61547, IEC (EN) 55015 and IEC (EN) 55022,Class B | Nos. | 25 | 1500 | 37500
49 | 100 x 50mm Size tray | Mts. | 75 | 550 | 41250
50 | 300 x 60mm Size tray | Mts. | 10 | 1450 | 14500
51 | 200 x 60mm Size tray | Mts. | 10 | 950 | 9500
52 | 100 x 60mm Size tray | Mts. | 25 | 550 | 13750
53 | 100 x 60mm Size tray | Mts. | 15 | 950 | 14250
54 | 300 x 40mm | Mts. | 5 | 2250 | 11250
55 | 250 x 40mm | Mts. | 8 | 1800 | 14400
56 | 200 x 40mm | Mts. | 8 | 1550 | 12400
57 | 150 x 40mm | Mts. | 10 | 1250 | 12500
58 | 100 x 40mm | Mts. | 35 | 950 | 33250
59 | 100 x 60mm Size | Mts. | 20 | 1250 | 25000
60 | 200 x 100mm Size(Powder coated) | Mts. | 5 | 2550 | 12750
61 | 150 x 100mm Size(Power-Powder coated) | Mts. | 5 | 2000 | 10000
62 | 350 x 350 x 50mm Size | Nos. | 1 | 4200 | 4200
63 | 300 x 300 x 50mm Size | Nos. | 4 | 2800 | 11200
64 | 250 x 250 x 50mm Size | Nos. | 4 | 2550 | 10200
65 | 200 x 200 x 50mm Size | Nos. | 4 | 2000 | 8000
66 | 150 x 150 x 50mm Size | Nos. | 15 | 1750 | 26250
67 | 110 x 110 x 50mm Size | Nos. | 30 | 1400 | 42000
68 | 32mm dia | Mts. | 15 | 45 | 675
69 | 25mm dia | Mts. | 200 | 40 | 8000
70 | 25mm dia floor | Mts. | 60 | 40 | 2400
71 | 19mm dia. Single Rod type Maintenance Free Earth pits. Rate shall include 450mm x 450mm x 300mm brick masonry chamber with CI frame and CI cover etc., complete. Eathing system shall be installed as per supplier guidelines /details. MS plate to be provided for each earth pit for its nomenclature. | Nos. | 2 | 20000 | 40000
72 | 25 x 3mm GI Earth flat | Mts. | 50 | 220 | 11000
73 | 25 x 6mm GI Earth flat | Mts. | 20 | 330 | 6600
74 | Busbar of 0.25 Mtr length made out of 25 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators along with glass enclosure. | Nos. | 2 | 2000 | 4000
75 | Busbar of 0.5 Mtr length made out of 25 x 3 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators along with enclosure. | Nos. | 2 | 3000 | 6000
76 | 8 SWG Cu Wire | Mts. | 10 | 750 | 7500
77 | Tinned copper Busbar of 0.5 Mtr length made out of 25 x 3 mm Cu. strip with drill holes of M8 at 25mm interval mounted on insulators with clear acrylic vision panel. | Nos. | 2 | 3000 | 6000
78 | 1 Core x 10 Sq. mm | Mts. | 250 | 292 | 73000
79 | End terminations | Mts. | 6 | 500 | 3000
80 | 1 Core x 6Sq. mm including Terminations | Mts. | 50 | 250 | 12500
81 | 1 Core x 4Sq. mm including Terminations | Mts. | 50 | 220 | 11000
82 | 1 Core x 2.5Sq. mm including Terminations | Mts. | 30 | 180 | 5400
83 | Rubber mat 1100V grade ISI approved - 2 m x 1m | Nos. | 2 | 6000 | 12000
84 | Shock treatment chart as approved by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting in 3 languages (Telugu , English & Hindi) | Nos. | 1 | 6000 | 6000
85 | First aid kit | Nos. | 1 | 4000 | 4000
86 | Danger boards | Nos. | 1 | 2500 | 2500
87 | Danger signage stickers on DB frames | Nos. | 1 | 300 | 300
88 | Supply & fixing of rubber gloves, gloves stand with wall mounting of Approved Make & as per supply voltage | Nos. | 1 | 5000 | 5000
89 | Laminated Schematic with glass frame | Nos. | 1 | 6000 | 6000
90 | Supply and Installation of DB Frame with wire ways shall be made out of 1.6mm thick CRCA sheet steel and powder coating colour shall match the colour of MCB DB's with hinged type door. 150mm x 100mm 1.6mm thick, wire ways / Raceway with 2mm thick screwed / press to fit cover with hinged type door for making Frame for MCB DB's. Complete required including installation accessories. | Rmt | 10 | 950 | 9500

## LIGHTING
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 2400mm LInear suspended Direct light fixture with with electronic driver Diffuser : Opal Diffuser with homogeneous light distribution without hotspots Housing material : Extruded Aluminum housing with Aluminum end cap Powder coating : Corrosion resistance Powder coated Light fixture to match to the workstation profile (end to end) | Nos. | 15 | 800 | 12000
2 | 1800mm LInear suspended Direct light fixture with with electronic driver Diffuser : Opal Diffuser with homogeneous light distribution without hotspots Housing material : Extruded Aluminum housing with Aluminum end cap Powder coating : Corrosion resistance Powder coated Light fixture to match to the workstation profile (end to end) | Nos. | 4 | 600 | 2400
3 | 1200mm LInear suspended Direct light fixture with with electronic driver Diffuser : Opal Diffuser with homogeneous light distribution without hotspots Housing material : Extruded Aluminum housing with Aluminum end cap Powder coating : Corrosion resistance Powder coated Light fixture to match to the workstation profile (end to end) | Nos. | 4 | 400 | 1600
4 | 15W/mtr 75MM SUSPENDED PROFILE LIGHT FIXTURE WITH ELECTRONIC DRIVER -4000K | Mtrs | 40 | 300 | 12000
5 | 2X2 Recess mount lighting fixture with electronic driver Diffuser : Opal Diffuser with homogeneous light distribution without hotspots Housing material : Extruded Aluminium Alloy Powder coating : Corrosion resistance Powder coated | Nos. | 8 | 400 | 3200
6 | 18W Recess mounted Downlight fixture with Electronic driver Diffuser : Opal Diffuser with homogeneous light distribution without hotspots Housing material : Aluminum Powder coating : Corrosion resistance Powder coated | Nos. | 60 | 300 | 18000
7 | 18W cylindrical suspended light with Electronic driver Housing material : Aluminum Powder coating : Corrosion resistance Powder coated Diameter varying from 100mm - 150mm | Nos. | 10 | 400 | 4000
8 | Suspended light as per look & feel ( Metallic paint finish - 1800 mm long ) | Nos. | 1 | 1000 | 1000
9 | Suspended light as per look & feel ( Metallic paint finish Ring Light 1200mm DIA ) | Nos. | 4 | 1000 | 4000
10 | Suspended light as per look & feel ( Dome Light 450mm DIA ) | Nos. | 4 | 500 | 2000

## UPS BOQ
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 10KVA CONVENTIONAL (3 phase in 3 phase out) UPS System in solo operation as specified complete with : Rectifier / Charger, Static inverter, Static switch & bypass changeover switch Controls, Switchgear, and all accessories with earthing as per the broad power scheme . The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. Also to include 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery breakers and the respective 6kVA UPS Units. The cable shall confirm to IS-694 and suitable end termination with all accessories, supports, MS base frames for load distribution, labelling etc complete to be considered. | No | 1 | 1033.4 | 250000
2 | Supply, Installation, Testing and commissiong of required 12Volts batteries for 10Kva UPS's with 15Mins back-up, Sealed maintenance free, Valve regulated type. Each battery bank shall be with one string. The Floor Loading shall not Exceed 400kg/sq.m. The Vendor shall include rate for required item such that floor loading shall not exceed 400Kg/sq.m. 300mm false floor is provided in the UPS & battery room. Battery cabinet with suitable ventilators, copper cables/buslinks between batteries, copper cables between UPS & batteries, DC MCCB Box, DC isolator panel for battery strings with suitable Tray system (DC Isolator box shall be individual for each UPS / Battery string). External Battery Circuit Breaker DC MCCB with Overload and short circuit ON ,OFF ,Trip, Led indicator with Spreader , Powder coated & MS enclosure Etc. The Battery rack should be modular in constrcution , Epoxy coated, anti acidic and fully insulated. Each battery to have end cap terminations. Floor loading shall not exeed 400Kg/sqmt. The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. (Battery monitoring system to be considered) | Set | 1 | 121015 | 100000
3 | 2KVA CONVENTIONAL (1 phase in 1 phase out) UPS System in solo operation as specified complete with : Rectifier / Charger, Static inverter, Static switch & bypass changeover switch Controls, Switchgear, and all accessories with earthing as per the broad power scheme . The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. Also to include 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery breakers and the respective 2kVA UPS Units. The cable shall confirm to IS-694 and suitable end termination with all accessories, supports, MS base frames for load distribution, labelling etc complete to be considered. | No | 1 | 211.4 | 45000
4 | Supply, Installation, Testing and commissiong of required 12Volts batteries for 2Kva UPS's with 30Mins back-up, Sealed maintenance free, Valve regulated type. Each battery bank shall be with one string. The Floor Loading shall not Exceed 400kg/sq.m. The Vendor shall include rate for required item such that floor loading shall not exceed 400Kg/sq.m. 300mm false floor is provided in the UPS & battery room. Battery cabinet with suitable ventilators, copper cables/buslinks between batteries, copper cables between UPS & batteries, DC MCCB Box, DC isolator panel for battery strings with suitable Tray system (DC Isolator box shall be individual for each UPS / Battery string). External Battery Circuit Breaker DC MCCB with Overload and short circuit ON ,OFF ,Trip, Led indicator with Spreader , Powder coated & MS enclosure Etc. The Battery rack should be modular in constrcution , Epoxy coated, anti acidic and fully insulated. Each battery to have end cap terminations. Floor loading shall not exeed 400Kg/sqmt. The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. (Battery monitoring system to be considered) | Set | 1 | 12230 | 20000
5 | 1KVA CONVENTIONAL (1 phase in 1 phase out) UPS System in solo operation as specified complete with : Rectifier / Charger, Static inverter, Static switch & bypass changeover switch Controls, Switchgear, and all accessories with earthing as per the broad power scheme . The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. Also to include 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery breakers and the respective 1kVA UPS Units. The cable shall confirm to IS-694 and suitable end termination with all accessories, supports, MS base frames for load distribution, labelling etc complete to be considered. | No | 1 | 111.4 | 25000
6 | Supply, Installation, Testing and commissiong of required 12Volts batteries for 1Kva UPS's with 90Mins back-up, Sealed maintenance free, Valve regulated type. Each battery bank shall be with one string. The Floor Loading shall not Exceed 400kg/sq.m. The Vendor shall include rate for required item such that floor loading shall not exceed 400Kg/sq.m. 300mm false floor is provided in the UPS & battery room. Battery cabinet with suitable ventilators, copper cables/buslinks between batteries, copper cables between UPS & batteries, DC MCCB Box, DC isolator panel for battery strings with suitable Tray system (DC Isolator box shall be individual for each UPS / Battery string). External Battery Circuit Breaker DC MCCB with Overload and short circuit ON ,OFF ,Trip, Led indicator with Spreader , Powder coated & MS enclosure Etc. The Battery rack should be modular in constrcution , Epoxy coated, anti acidic and fully insulated. Each battery to have end cap terminations. Floor loading shall not exeed 400Kg/sqmt. The Vendor shall inculde rate for required item such that floor loading shall not exceed 400Kg/sq.m. (Battery monitoring system to be considered) | Set | 1 | 12190 | 15000

## VRF SYSTEM
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Outdoor Unit(ODU) : Cooling Capacity :28 HP (OFFICE AREA)( combination of modules will be inline with the OEM) | Set | 1 | 40000 | 40000
2 | Outdoor Unit(ODU) : Cooling Capacity :6 HP (CRITICAL ARAE) - 1W+1S | Set | 2 | 10000 | 20000
3 | Serving Area: BATTERY ROOM 1.0 TR Hi wall unit along with drain pump | Nos | 2 | 2500 | 5000
4 | Serving Area: UPS ROOM 1.5 TR Hi wall unit along | Nos | 2 | 2500 | 5000
5 | Serving Area: SERVER ROOM 2.0 TR Hi wall unit along with drain pump | Nos | 2 | 2500 | 5000
6 | Serving Area: 0.8 TR cassette Ac unit | Nos | 1 | 3000 | 3000
7 | Serving Area: 1.0 TR cassette Ac unit | Nos | 3 | 3000 | 9000
8 | Serving Area: 1.5 TR cassette Ac unit | Nos | 11 | 3000 | 33000
9 | Serving Area: 2.65 TR cassette Ac unit | Nos | 2 | 3000 | 6000
10 | 28.6mm OD (insulation =19 mm thick) | Rmt | 30 | 250 | 7500
11 | 22.2mm OD (insulation =13 mm thick) | Rmt | 30 | 200 | 6000
12 | 19.1mm OD (insulation =13 mm thick) | Rmt | 60 | 200 | 12000
13 | 15.9mm OD (insulation =13 mm thick) | Rmt | 50 | 150 | 7500
14 | 12.7mm OD (insulation =13 mm thick) | Rmt | 40 | 150 | 6000
15 | 9.5mm OD (insulation =13 mm thick) | Rmt | 50 | 100 | 5000
16 | 6.4mm OD (insulation =13 mm thick) | Rmt | 50 | 100 | 5000
17 | 40 mm dia | Rmt | 20 | 40 | 800
18 | 32 mm dia | Rmt | 30 | 40 | 1200
19 | 25 mm dia | Rmt | 50 | 40 | 2000
20 | Electrical Cable between Isolator to ODU.Suitable size copper flexible cable with necessary earthing insulation | Rmt | 15 | 40 | 600
21 | Providing & fixing of 2 Cx 1.5 sqmm cu. cable for control cum trans-mission between Indoor unit and Out Door Unit through PVC Conduit. | Rmt | 155 | 30 | 4650
22 | Imported fittings like Y-Joints and headers etc as per the layout( additional supports should consider for both ends of the Y joint) | Nos | 22 | 500 | 11000
23 | Supply & providing of MS stand for VRV ODU along with proper supports-suitable for above configuration | Set | 4 | 1000 | 4000
24 | Filling, testing, commissioning including topping up of R410 A Refrigerant. | Kg | 25 | 200 | 5000
25 | size:150x 50mm(14 SWG grade)-2mm thick | Rmt | 75 | 100 | 7500
26 | size:300x 100mm with cover (14 SWG grade)-2mm thick Only for Exposed & Vertical shaft area | Rmt | 75 | 200 | 15000
27 | Supply & installation,testing & comissioning of Centarl controller integrating all floor Indoor units with necessary software & spare parts | Lot | 1 | 10000 | 10000

## VRF LOWSIDE
SL NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | 850 Cfm - 25 mm external static cabinet type fresh air fan with prefilter & necessary supports (Office Fresh air) STARTER PANEL PROVIDED BY ELECTRICAL VENDOR, along with MERV-08 | Nos | 1 | 8700 | 8700
2 | 300 Cfm - 15 mm external static single skin Inline fan with all necessary supports. (Toilet exhaust). Fan shall be provided with in built fan regulator. | Nos | 1 | 2325 | 2325
3 | 300 Cfm - 15 mm external static single skin Inline fan with all necessary supports. (Pantry exhaust). Fan shall be provided with in built fan regulator. | Nos | 1 | 2325 | 2325
4 | 100 Cfm - 30 mm external static single skin Inline fan with all necessary supports. (Battery room exhaust). Timer control panel should be considered | Nos | 1 | 1575 | 1575
5 | 24 G Ducting with TDF flanges(0-750mm) | Sqm | 100 | 200 | 20000
6 | 22 G Ducting with TDF flanges(751-1200mm) | Sqm | 50 | 200 | 10000
7 | 375 x 375 MM (Neck Size) | Nos | 1 | 200 | 200
8 | Powder Coated linear grilles for supply and return distribution ( colour for the grill to b confirmed by Arch/ PMC team before placing the order) . Deflection of the grille shall be 0 / 15 / 30. same will be confirmed later. Single / 2 way / 4 way deflection shall be confirmed later. | Sqm | 4 | 1000 | 4000
9 | Collar Dampers of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (quantity including for diffusers & grills) | Sqm | 3 | 1000 | 3000
10 | 160mm dia | Nos | 2 | 500 | 1000
11 | Volume Control Dampers made out of 100 x 40 x 1.2 mm thick galavanised steel frame and blades of 1.55 mm galavanised sheet steel. For Rectangular & elliptical duct. | Sqm | 2 | 1000 | 2000
12 | 150 mm dia | Rmt | 30 | 200 | 6000
13 | 150 mm dia | Nos | 19 | 200 | 3800
14 | 150mm dia | Rmt | 15 | 200 | 3000
15 | Supply,installation,testing & comissioning of 525 x 525 x 450 mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible connection from the main duct. | Nos | 1 | 950 | 950
16 | Supply and installation of Acrylic fire stop sealant CP606 or Approved Equivalent )with minimum 2 hours fire rating when tested in accordance with UL 1479 standards, shall be used along the periphery of ducts & chiller pipes without insulation passing through fire rated walls and floors made of concrete, masonry, metal, gypsum construction to provide up to 2 hours insulation and integrity when subject to the test conditions of UL 1479 standards. The product shall also be age tested as per DafStb guidelines. Sealant to provide sufficient MAF, water and gas tight seal apart from providing an airborne sound transmission reduction (STC of 50) and shall be tested as per DIN 52210 for sound insulation . The product should be tested for mold resistance rating of 0 as determined by ASTM G21-96 and should have a VOC content of approx. 75 g/l as per LEED 2009. The sealant shall be FM approved. All installations to be in full accordance with the manufacturer. The sealant should be tested in accordance with IEC 60068-2-57:1999-11 (Environmental Testing) as per Part 2-57: Test for Vibration-Time-history method and VERTEQII for seismic zone 4. The product shall bear the UL and FM approval logo on the packing where applicable. The rate shall include the mineral wool backing material and other miscellaneous items etc.., Assumed 15% Penetrants Ocupancy. Firestop installation should be done by HAFSC ( Accredated Firestop Speciality Contractor by providing complete installation report using CFS DM). Or using FIT (Firestop Installer Training) Program. As per IFC Guideliness EJ is recomended for non standard openings.-( supply & return air ducts.) | Sqm | 2 | 400 | 800
17 | Supply Fabrication , and erection of Double canvas connection made out of fire retardent canvas cloth with Zip required necessary fixing arrangements including nuts & bolts Etc | Sqm | 5 | 500 | 2500
18 | 15 mm thick With aluminium foil | Sqm | 30 | 200 | 6000
19 | 9 mm thick | Sqm | 120 | 100 | 12000
20 | Under Deck Insulation of specified 16mm thickness of Elastromeric rubber insulation of Class "O" manafactured as per ASTM E 84 test & which should also meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape (Black Cotton Tape not acceptable). | Sqm | 250 | 100 | 25000
21 | Supply installation , testing & commissioning of sequential control panel all necessary supporting materials | NOS | 3 | 5000 | 15000
22 | 1.2 m WIDE- suitable for double door | Nos | 1 | 5000 | 5000
23 | Pedestals : Providing & Laying of Reinforced cement concrete of M20 grade at the level given below, using river sand, 20 mm as down size coarse aggregates, application of necessary admixtures as specified by consultants inclding all leads and lifst, scaffolding wheever necessary, curing as directed, including the cost of shuttering, centering and staging for required height. | cum | 2 | 1000 | 2000
24 | Chipping, chassing & Plastering the wall openings in cement mortor 1:6 of 15 mm thick finishing to line and level with sand faced finshing at all levels, including all leads & lifts, scaffolding, curing etc complete (for SA & RA openings in ahu rooms, opgs for CHW pipes etc) | sqm | 2 | 100 | 200